## Sheet1
General data | [19 empty] | Materials |  |  |  | ITER Classification | [11 empty] | Leak requirements |  | Fluid parameters | [9 empty] | Environment |  |  |  |  | Actuator characteristics |  |  |  |  | PRV / RD characteristics |  |  |  | Check valves characteristics |  |  |  |  | I&C | Fire Protection
New Tag | Reference | New Line Number | Valve Code | Valve # | Scope/PBS | PID | Engineering Description | Valve position during normal operation | Function | Actuator type | Actuator Action | DN (in=out) [mm] | DN (in=out) [in] | Steam Seal Type | Room | Fail Position | Lock Position | Wedge/Disc Type | End Connection | Material - Body, Bonnet | Material - Stem, Ball, Disc, Plug | Material - Seat | Material Composition Requirement [Co, Nb, Ta] | Functional SIC classification | Train | PIC | Safety Function | QC | SC | VC | TC | ESPN | SIV | Fluid Group | PED | Tot Piping External Leak Tightness [Pa.m3.s-1] | Internal Leak Tightness | Fluid | Tope (deg) | Pope (bara) | Max Allowable Pressure PS (barg) | Pressure test (bar) | Td (deg) | Max Ambient T (deg) | Max Ambient P (bara) | ASME Class or PN, EN1092 | Nominal Flowrate (Nm3/h) | Neutron Flux (n/cm2.s) | Static Magnetic Field (mT) | Radiological zoning - Mode 0 | Radiological zoning - Mode 1 | Radiological zoning - Mode 2 | Actuator Control | Max DP Opening/Closing (bar) | Compressed Air supply (barg) | Mechanical Stop Yes/No | Required Stroke Time [s] [MIN, MAX] | Required relieving capacity (kg/h) | Set pressure (barg) | Atmospheric discharge | Superimposed backpressure (bar) | Check Valve Type | Min Closure time (s) | Max fluid deceleration (m/s2) | Max reverse fluid velocity (m/s) | Forward flow rate (m3/h) | Position indication | Fire Sectorization | Max Fire T (C) | Thermal Insulation Type
24VPHM-VG-1058 | VG-1058 | 24VPHM-PI-2072 | VG | 1058 | 24VPHM | 24VPHM-PID-001/10 | Pneumatic Ball Valve | Open | Isolate | Pneumatic | Spring return | 100 | 4 | Packing BH - EN 15848 | 11-B2-01 | Fail Close | N/A | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | N/A | N/A | N/A | II | N/A | N/A | Rate C - EN 12266 | Air | 35 | 1 | 0.5 | 0.92391 | 125 | 130 | 2 | PN10 | 350 | 10000 | 20 | Red | Yellow | Red | On/Off | 1.5 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-1158 | VG-1158 | 24VPHM-PI-2074 | VG | 1158 | 24VPHM | 24VPHM-PID-001/10 | Pneumatic Ball Valve | Open | Isolate | Pneumatic | Spring return | 100 | 4 | Packing BH - EN 15848 | 11-B2-01 | Fail Close | N/A | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | N/A | N/A | N/A | II | N/A | N/A | Rate C - EN 12266 | Air | 35 | 1 | 0.5 | 0.92391 | 125 | 130 | 2 | PN10 | 350 | 10000 | 20 | Red | Yellow | Red | On/Off | 1.5 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VP00-VG-1211 | VG-1211 | 24VP00-PI-1311 | VG | 1211 | 24VP00 | 24VP00-PID-001/02 | Pneumatic Ball Valve | Closed | Isolate | Pneumatic | Spring Return | 50 | 2 | Packing BH - EN 15848 | 11-B2-01 | Fail open | N/A | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 10 | 4.8 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 15 | 10000 | 20 | Red | Yellow | Red | On/Off | 9 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VP00-VG-1313 | VG-1313 | 24VP00-PI-1313 | VG | 1313 | 24VP00 | 24VP00-PID-001/02 | Manual Ball Valve | Closed | Isolate | Manual | N/A | 50 | 2 | Packing BH - EN 15848 | 11-B2-01 | N/A | LO | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 10 | 3.5 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 15 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 142 | Passive
24VP00-VG-1314 | VG-1314 | 24VP00-PI-1314 | VG | 1314 | 24VP00 | 24VP00-PID-001/02 | Manual Ball Valve | Closed | Isolate | Manual | N/A | 25 | 1 | Packing BH - EN 15848 | 11-B2-01 | N/A | LC | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 10 | 3.5 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 5 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 142 | Passive
24VP00-VG-1315 | VG-1315 | 24VP00-PI-1315 | VG | 1315 | 24VP00 | 24VP00-PID-001/02 | Manual Ball Valve | Closed | Isolate | Manual | N/A | 25 | 1 | Packing BH - EN 15848 | 11-B2-01 | N/A | LC | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 10 | 3.5 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 5 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 142 | Passive
24VPHM-VG-3201 | VG-3201 | 24VPHM-PI-3001 | VG | 3201 | 24VPHM | 24VPHM-PID-001/11 | Pneumatic Ball Valve | Open | Isolate | Pneumatic | Double Acting | 65 | 2.5 | Packing BH - EN 15848 | 11-B2-01 | Fail in Position | N/A | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 6 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 25 | 10000 | 20 | Red | Yellow | Red | On/Off | 9 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-3203 | VG-3203 | 24VPHM-PI-3003 | VG | 3203 | 24VPHM | 24VPHM-PID-001/11 | Pneumatic Ball Valve | Open | Isolate | Pneumatic | Double Acting | 65 | 2.5 | Packing BH - EN 15848 | 11-B2-01 | Fail in Position | N/A | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 14 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 25 | 10000 | 20 | Red | Yellow | Red | On/Off | 9 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-3211 | VG-3211 | 24VPHM-PI-3101 | VG | 3211 | 24VPHM | 24VPHM-PID-001/11 | Pneumatic Ball Valve | Open | Isolate | Pneumatic | Double Acting | 65 | 2.5 | Packing BH - EN 15848 | 11-B1-01 | Fail in Position | N/A | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 6 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 25 | 10000 | 20 | Red | Yellow | Red | On/Off | 9 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VPHM-VG-3213 | VG-3213 | 24VPHM-PI-3103 | VG | 3213 | 24VPHM | 24VPHM-PID-001/11 | Pneumatic Ball Valve | Open | Isolate | Pneumatic | Double Acting | 65 | 2.5 | Packing BH - EN 15848 | 11-B1-01 | Fail in Position | N/A | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 14 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 25 | 10000 | 20 | Red | Yellow | Red | On/Off | 9 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VPHM-VG-3351 | VG-3351 | 24VPHM-PI-3002 | VG | 3351 | 24VPHM | 24VPHM-PID-001/02 | Manual Ball Valve | Open | Isolate | Manual | N/A | 65 | 2.5 | Packing BH - EN 15848 | 11-B2-01 | N/A | LO | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 7 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 25 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 142 | Passive
24VPHM-VG-3353 | VG-3353 | 24VPHM-PI-3003 | VG | 3353 | 24VPHM | 24VPHM-PID-001/02 | Manual Ball Valve | Open | Isolate | Manual | N/A | 65 | 2.5 | Packing BH - EN 15848 | 11-B2-01 | N/A | LO | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 14 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 25 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 142 | Passive
24VPHM-VG-3355 | VG-3355 | 24VPHM-PI-3102 | VG | 3355 | 24VPHM | 24VPHM-PID-001/02 | Manual Ball Valve | Open | Isolate | Manual | N/A | 65 | 2.5 | Packing BH - EN 15848 | 11-B2-01 | N/A | LO | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 7 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 25 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 142 | Passive
24VPHM-VG-3357 | VG-3357 | 24VPHM-PI-3103 | VG | 3357 | 24VPHM | 24VPHM-PID-001/02 | Manual Ball Valve | Open | Isolate | Manual | N/A | 65 | 2.5 | Packing BH - EN 15848 | 11-B2-01 | N/A | LO | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 14 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 25 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 142 | Passive
24VPHM-VG-3391 | VG-3391 | 24VPHM-PI-3001 | VG | 3391 | 24VPHM | 24VPHM-PID-001/07 | Manual Ball Valve | Open | Isolate | Manual | N/A | 65 | 2.5 | Packing BH - EN 15848 | 11-B1-01 | N/A | LO | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 6 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 25 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 142 | Passive
24VPHM-VG-3392 | VG-3392 | 24VPHM-PI-3002 | VG | 3392 | 24VPHM | 24VPHM-PID-001/07 | Manual Ball Valve | Open | Isolate | Manual | N/A | 65 | 2.5 | Packing BH - EN 15848 | 11-B1-01 | N/A | LO | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 7 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 25 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-3393 | VG-3393 | 24VPHM-PI-3101 | VG | 3393 | 24VPHM | 24VPHM-PID-001/07 | Manual Ball Valve | Open | Isolate | Manual | N/A | 65 | 2.5 | N/A | 11-B1-01 | N/A | LO | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 6 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 25 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-3394 | VG-3394 | 24VPHM-PI-3102 | VG | 3394 | 24VPHM | 24VPHM-PID-001/07 | Manual Ball Valve | Open | Isolate | Manual | N/A | 65 | 2.5 | N/A | 11-B1-01 | N/A | LO | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 7 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 25 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-4001 | VG-4001 | 24VPHM-PI-4301 | VG | 4001 | 24VPHM | 24VPHM-PID-001/14 | Pneumatic Ball Valve | Closed | Isolate | Pneumatic | Spring return | 80 | 3 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 45 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VPHM-VG-4002 | VG-4002 | 24VPHM-PI-4308 | VG | 4002 | 24VPHM | 24VPHM-PID-001/14 | Pneumatic Ball Valve | Closed | Isolate | Pneumatic | Spring return | 80 | 3 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 45 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 905 | Passive
24VP00-VG-4201 | VG-4201 | 24VP00-PI-4301 | VG | 4201 | 24VP00 | 24VP00-PID-001/07 | Pneumatic Ball Valve | Closed | Isolate | Pneumatic | Spring return | 80 | 3 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 45 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VP00-VG-4213 | VG-4213 | 24VP00-PI-4313 | VG | 4213 | 24VP00 | 24VP00-PID-001/02 | Pneumatic Ball Valve | Closed | Isolate | Pneumatic | Spring return | 40 | 1.5 | Packing BH - EN 15848 | 11-B2-01 | Fail Close | N/A | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VP00-VG-4303 | VG-4303 | 24VP00-PI-4303 | VG | 4303 | 24VP00 | 24VP00-PID-001/07 | Manual Ball Valve | Closed | Isolate | Manual | N/A | 15 | 0.5 | Packing BH - EN 15848 | 11-B1-01 | N/A | N/A | N/A | Welded | EN 1.4307, grade 304L | 304L | TBD | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | Non-SC | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-5101 | VG-5101 | 24VPHM-PI-5101 | VG | 5101 | 24VPHM | 24VPHM-PID-001/12 | Pneumatic Ball Valve | Closed | Isolate | Pneumatic | Double Acting | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | N/A | Welded - Top Entry | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
Note on BS2: Tallarigo Alberto: Passive: no need to keep hot/cold internal condition