## Sheet1
General data | [19 empty] | Materials |  |  |  | ITER Classification | [11 empty] | Leak requirements |  | Fluid parameters | [9 empty] | Environment |  |  |  |  | Actuator characteristics |  |  |  |  | PRV / RD characteristics |  |  |  | Check valves characteristics |  |  |  |  | I&C | Fire Protection
New Tag | Reference | New Line Number | Valve Code | Valve # | Scope/PBS | PID | Engineering Description | Valve position during normal operation | Function | Actuator type | Actuator Action | DN (in=out) [mm] | DN (in=out) [in] | Steam Seal Type | Room | Fail Position | Lock Position | Wedge/Disc Type | End Connection | Material - Body, Bonnet | Material - Stem, Ball, Disc, Plug | Material - Seat | Material Composition Requirement [Co, Nb, Ta] | Functional SIC classification | Train | PIC | Safety Function | QC | SC | VC | TC | ESPN | SIV | Fluid Group | PED | Tot Piping External Leak Tightness [Pa.m3.s-1] | Internal Leak Tightness | Fluid | Tope (deg) | Pope (bara) | Max Allowable Pressure PS (barg) | Pressure test (bar) | Td (deg) | Max Ambient T (deg) | Max Ambient P (bara) | ASME Class or PN, EN1092 | Nominal Flowrate (Nm3/h) | Neutron Flux (n/cm2.s) | Static Magnetic Field (mT) | Radiological zoning - Mode 0 | Radiological zoning - Mode 1 | Radiological zoning - Mode 2 | Actuator Control | Max DP Opening/Closing (bar) | Compressed Air supply (barg) | Mechanical Stop Yes/No | Required Stroke Time [s] [MIN, MAX] | Required relieving capacity (kg/h) | Set pressure (barg) | Atmospheric discharge | Superimposed backpressure (bar) | Check Valve Type | Min Closure time (s) | Max fluid deceleration (m/s2) | Max reverse fluid velocity (m/s) | Forward flow rate (m3/h) | Position indication | Fire Sectorization | Max Fire T (C) | Thermal Insulation Type
24VP00-VG-1024 | VG-1024 | 24VP00-PI-1501 | VG | 1024 | 24VP00 | 24VP00-PID-001/03 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 15 | 0.5 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | TC-2A | N/A | N/A | II | N/A | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 125 | 0.5 | 0.5 | 1.0316 | 250 | 145 | 1.6 | PN10 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 1.5 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 905 | Passive
24VPHM-VG-1392 | VG-1392 | 24VPHM-PI-1593 | VG | 1392 | 24VPHM | 24VPHM-PID-001/08 | Manual Globe Valve | Closed | Isolate | No actuator | N/A | 15 | 0.5 | Packing BH - EN 15848 | 11-L3-02E | N/A | N/A | N/A | Welded | EN 1.4307, grade 304L | 304L | 304L | According to EN standard | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | TC-2A | N/A | N/A | I | N/A | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 15 | 0.75 | 0.5 | 0.92391 | 80 | 130 | 1.2 | PN10 | 700 | 100000 | 125 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-04 | ISO 834 | Passive
24VPHM-VG-3301 | VG-3301 | 24VPHM-PI-3501 | VG | 3301 | 24VPHM | 24VPHM-PID-001/11 | Manual Globe Valve | Closed | Isolate | Manual | N/A | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | N/A | LC | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 6 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 5 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-3302 | VG-3302 | 24VPHM-PINST-3201 | VG | 3302 | 24VPHM | 24VPHM-PID-001/11 | Manual Globe Valve | Open | Isolate | Manual | N/A | 15 | 0.5 | Packing BH - EN 15848 | 11-B1-01 | N/A | LO | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 6 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 1 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-3303 | VG-3303 | 24VPHM-PINST-3201 | VG | 3303 | 24VPHM | 24VPHM-PID-001/11 | Manual Globe Valve | Open | Isolate | Manual | N/A | 15 | 0.5 | Packing BH - EN 15848 | 11-B1-01 | N/A | LO | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 6 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 1 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-3304 | VG-3304 | 24VPHM-PI-3503 | VG | 3304 | 24VPHM | 24VPHM-PID-001/11 | Manual Globe Valve | Closed | Isolate | Manual | N/A | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | N/A | LC | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 14 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 5 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-3305 | VG-3305 | 24VPHM-PINST-3242 | VG | 3305 | 24VPHM | 24VPHM-PID-001/11 | Manual Globe Valve | Open | Isolate | Manual | N/A | 15 | 0.5 | Packing BH - EN 15848 | 11-B1-01 | N/A | LO | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 14 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 1 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-3306 | VG-3306 | 24VPHM-PINST-3242 | VG | 3306 | 24VPHM | 24VPHM-PID-001/11 | Manual Globe Valve | Open | Isolate | Manual | N/A | 15 | 0.5 | Packing BH - EN 15848 | 11-B1-01 | N/A | LO | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 14 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 1 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 142 | Passive
24VPHM-VG-3311 | VG-3311 | 24VPHM-PI-3502 | VG | 3311 | 24VPHM | 24VPHM-PID-001/11 | Manual Globe Valve | Closed | Isolate | Manual | N/A | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | N/A | LC | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 6 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 5 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-3312 | VG-3312 | 24VPHM-PINST-3101 | VG | 3312 | 24VPHM | 24VPHM-PID-001/11 | Manual Globe Valve | Open | Isolate | Manual | N/A | 15 | 0.5 | Packing BH - EN 15848 | 11-B1-01 | N/A | LO | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 6 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 1 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-3313 | VG-3313 | 24VPHM-PINST-3101 | VG | 3313 | 24VPHM | 24VPHM-PID-001/11 | Manual Globe Valve | Open | Isolate | Manual | N/A | 15 | 0.5 | Packing BH - EN 15848 | 11-B1-01 | N/A | LO | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 6 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 1 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-3314 | VG-3314 | 24VPHM-PI-3504 | VG | 3314 | 24VPHM | 24VPHM-PID-001/11 | Manual Globe Valve | Closed | Isolate | Manual | N/A | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | N/A | LC | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 14 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 5 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-3315 | VG-3315 | 24VPHM-PINST-3142 | VG | 3315 | 24VPHM | 24VPHM-PID-001/11 | Manual Globe Valve | Open | Isolate | Manual | N/A | 15 | 0.5 | Packing BH - EN 15848 | 11-B1-01 | N/A | LO | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 14 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 1 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-3316 | VG-3316 | 24VPHM-PINST-3142 | VG | 3316 | 24VPHM | 24VPHM-PID-001/11 | Manual Globe Valve | Open | Isolate | Manual | N/A | 15 | 0.5 | Packing BH - EN 15848 | 11-B1-01 | N/A | LO | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 14 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 1 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-3352 | VG-3352 | 24VPHM-PI-3224 | VG | 3352 | 24VPHM | 24VPHM-PID-001/02 | Manual Globe Valve | Closed | Isolate | Manual | N/A | 25 | 1 | Packing BH - EN 15848 | 11-B2-01 | N/A | LC | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 7 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 5 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 142 | Passive
24VPHM-VG-3354 | VG-3354 | 24VPHM-PI-3241 | VG | 3354 | 24VPHM | 24VPHM-PID-001/02 | Manual Globe Valve | Closed | Isolate | Manual | N/A | 25 | 1 | Packing BH - EN 15848 | 11-B2-01 | N/A | LC | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 14 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 5 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 142 | Passive
24VPHM-VG-3356 | VG-3356 | 24VPHM-PI-3324 | VG | 3356 | 24VPHM | 24VPHM-PID-001/02 | Manual Globe Valve | Closed | Isolate | Manual | N/A | 25 | 1 | Packing BH - EN 15848 | 11-B2-01 | N/A | LC | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 7 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 5 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 142 | Passive
24VPHM-VG-3358 | VG-3358 | 24VPHM-PI-3341 | VG | 3358 | 24VPHM | 24VPHM-PID-001/02 | Manual Globe Valve | Closed | Isolate | Manual | N/A | 25 | 1 | Packing BH - EN 15848 | 11-B2-01 | N/A | LC | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 14 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 5 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 142 | Passive
24VPHM-VG-3395 | VG-3395 | 24VPHM-PI-3505 | VG | 3395 | 24VPHM | 24VPHM-PID-001/07 | Manual Globe Valve | Closed | Isolate | Manual | N/A | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | N/A | LC | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 6 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 5 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-3396 | VG-3396 | 24VPHM-PI-3506 | VG | 3396 | 24VPHM | 24VPHM-PID-001/07 | Manual Globe Valve | Closed | Isolate | Manual | N/A | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | N/A | LC | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 7 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 5 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-3397 | VG-3397 | 24VPHM-PI-3507 | VG | 3397 | 24VPHM | 24VPHM-PID-001/07 | Manual Globe Valve | Closed | Isolate | Manual | N/A | 25 | 1 | N/A | 11-B1-01 | N/A | LC | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 6 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 5 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-3398 | VG-3398 | 24VPHM-PI-3508 | VG | 3398 | 24VPHM | 24VPHM-PID-001/07 | Manual Globe Valve | Closed | Isolate | Manual | N/A | 25 | 1 | N/A | 11-B1-01 | N/A | LC | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 7 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 5 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VP00-VG-4208 | VG-4208 | 24VP00-PI-4302 | VG | 4208 | 24VP00 | 24VP00-PID-001/09 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Packing BH - EN 15848 | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 5 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VP00-VG-4212 | VG-4212 | 24VP00-PI-4312 | VG | 4212 | 24VP00 | 24VP00-PID-001/10 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring Return | 40 | 1.5 | Packing BH - EN 15848 | 11-B2-01 | Fail Close | N/A | N/A | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-4256 | VG-4256 | 24VPHM-PI-4356 | VG | 4256 | 24VPHM | 24VPHM-PID-001/02 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 40 | 1.5 | Packing BH - EN 15848 | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-4272 | VG-4272 | 24VPHM-PI-4372 | VG | 4272 | 24VPHM | 24VPHM-PID-001/05 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 40 | 1.5 | Packing BH - EN 15848 | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-4282 | VG-4282 | 24VPHM-PI-4382 | VG | 4282 | 24VPHM | 24VPHM-PID-001/06 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 40 | 1.5 | Packing BH - EN 15848 | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VP00-VG-4302 | VG-4302 | 24VP00-PI-4302 | VG | 4302 | 24VP00 | 24VP00-PID-001/07 | Manual Globe Valve | Open | Isolate | Manual | N/A | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | N/A | LP | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 5 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-4302 | VG-4302 | 24VPHM-PI-4309 | VG | 4302 | 24VPHM | 24VPHM-PID-001/14 | Manual Globe Valve | Open | Isolate | Manual | N/A | 15 | 0.5 | Packing BH - EN 15848 | 11-B1-01 | N/A | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 6 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 1 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-4303 | VG-4303 | 24VPHM-PI-4310 | VG | 4303 | 24VPHM | 24VPHM-PID-001/14 | Manual Globe Valve | Open | Isolate | Manual | N/A | 15 | 0.5 | Packing BH - EN 15848 | 11-B1-01 | N/A | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 6 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 1 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VP00-VG-4311 | VG-4311 | 24VP00-PI-4301 | VG | 4311 | 24VP00 | 24VP00-PID-001/07 | Manual Globe Valve | Open | Isolate | Manual | N/A | 80 | 3 | Packing BH - EN 15848 | 11-B2-01 | N/A | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 142 | Passive
24VP00-VG-4312 | VG-4312 | 24VP00-PI-4312 | VG | 4312 | 24VP00 | 24VP00-PID-001/07 | Manual Globe Valve | Open | Isolate | Manual | N/A | 40 | 1.5 | Packing BH - EN 15848 | 11-B2-01 | N/A | LP | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 142 | Passive
24VPHM-VG-4351 | VG-4351 | 24VPHM-PI-4351 | VG | 4351 | 24VPHM | 24VPHM-PID-001/14 | Manual Globe Valve | Open | Isolate | Manual | N/A | 50 | 2 | Packing BH - EN 15848 | 11-B1-01 | N/A | LP | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-4356 | VG-4356 | 24VPHM-PI-4356 | VG | 4356 | 24VPHM | 24VPHM-PID-001/14 | Manual Globe Valve | Open | Isolate | Manual | N/A | 40 | 1.5 | Packing BH - EN 15848 | 11-B1-01 | N/A | LP | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-4370 | VG-4370 | 24VPHM-PI-4370 | VG | 4370 | 24VPHM | 24VPHM-PID-001/14 | Manual Globe Valve | Open | Isolate | Manual | N/A | 40 | 1.5 | Packing BH - EN 15848 | 11-B1-01 | N/A | LP | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-4372 | VG-4372 | 24VPHM-PI-4372 | VG | 4372 | 24VPHM | 24VPHM-PID-001/14 | Manual Globe Valve | Open | Isolate | Manual | N/A | 40 | 1.5 | Packing BH - EN 15848 | 11-B1-01 | N/A | LP | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 142 | Passive
24VPHM-VG-4380 | VG-4380 | 24VPHM-PI-4380 | VG | 4380 | 24VPHM | 24VPHM-PID-001/14 | Manual Globe Valve | Open | Isolate | Manual | N/A | 40 | 1.5 | Packing BH - EN 15848 | 11-B1-01 | N/A | LP | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-4382 | VG-4382 | 24VPHM-PI-4382 | VG | 4382 | 24VPHM | 24VPHM-PID-001/14 | Manual Globe Valve | Open | Isolate | Manual | N/A | 40 | 1.5 | Packing BH - EN 15848 | 11-B1-01 | N/A | LP | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 142 | Passive
24VPHM-VG-4390 | VG-4390 | 24VPHM-PI-4390 | VG | 4390 | 24VPHM | 24VPHM-PID-001/14 | Manual Globe Valve | Open | Isolate | Manual | N/A | 40 | 1.5 | Packing BH - EN 15848 | 11-B1-01 | N/A | LP | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VP00-VG-5003 | VG-5003 | 24VP00-PI-5003 | VG | 5003 | 24VP00 | 24VP00-PID-001/06 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | N/A | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-5014 | VG-5014 | 24VP00-PI-5014 | VG | 5014 | 24VP00 | 24VP00-PID-001/02 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | N/A | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-5017 | VG-5017 | 24VP00-PI-5017 | VG | 5017 | 24VP00 | 24VP00-PID-001/02 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N/A | N/A | I | SEP | 1e-05 | Rate B - EN 12266 | Nitrogen Gas | 25 | 1.5 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 2.5 | 7 | YES | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-5027 | VG-5027 | 24VP00-PI-5027 | VG | 5027 | 24VP00 | 24VP00-PID-001/03 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N/A | N/A | I | SEP | 1e-05 | Rate B - EN 12266 | Nitrogen Gas | 25 | 1.5 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 2.5 | 7 | YES | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-5037 | VG-5037 | 24VP00-PI-5037 | VG | 5037 | 24VP00 | 24VP00-PID-001/04 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N/A | N/A | I | SEP | 1e-05 | Rate B - EN 12266 | Nitrogen Gas | 25 | 1.5 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 2.5 | 7 | YES | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-5047 | VG-5047 | 24VP00-PI-5047 | VG | 5047 | 24VP00 | 24VP00-PID-001/05 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N/A | N/A | I | SEP | 1e-05 | Rate B - EN 12266 | Nitrogen Gas | 25 | 1.5 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 2.5 | 7 | YES | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VPHM-VG-5051 | VG-5051 | 24VPHM-PI-5101 | VG | 5051 | 24VPHM | 24VPHM-PID-001/02 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N/A | N/A | I | SEP | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 1.5 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 2.5 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VP00-VG-5103 | VG-5103 | 24VP00-PI-5103 | VG | 5103 | 24VP00 | 24VP00-PID-001/06 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | N/A | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-5114 | VG-5114 | 24VP00-PI-5114 | VG | 5114 | 24VP00 | 24VP00-PID-001/02 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | N/A | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-5117 | VG-5117 | 24VP00-PI-5117 | VG | 5117 | 24VP00 | 24VP00-PID-001/02 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N/A | N/A | I | SEP | 1e-05 | Rate B - EN 12266 | Nitrogen Gas | 25 | 1.5 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 2.5 | 7 | YES | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-5127 | VG-5127 | 24VP00-PI-5127 | VG | 5127 | 24VP00 | 24VP00-PID-001/03 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N/A | N/A | I | SEP | 1e-05 | Rate B - EN 12266 | Nitrogen Gas | 25 | 1.5 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 2.5 | 7 | YES | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-5137 | VG-5137 | 24VP00-PI-5137 | VG | 5137 | 24VP00 | 24VP00-PID-001/04 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N/A | N/A | I | SEP | 1e-05 | Rate B - EN 12266 | Nitrogen Gas | 25 | 1.5 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 2.5 | 7 | YES | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-5147 | VG-5147 | 24VP00-PI-5147 | VG | 5147 | 24VP00 | 24VP00-PID-001/05 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N/A | N/A | I | SEP | 1e-05 | Rate B - EN 12266 | Nitrogen Gas | 25 | 1.5 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 2.5 | 7 | YES | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-5202 | VG-5202 | 24VP00-PI-5002 | VG | 5202 | 24VP00 | 24VP00-PID-001/06 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Double Acting | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | Fail in Position | N/A | N/A | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-5203 | VG-5203 | 24VP00-PI-5102 | VG | 5203 | 24VP00 | 24VP00-PID-001/06 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Double Acting | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | Fail in Position | N/A | N/A | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VPHM-VG-5255 | VG-5255 | 24VPHM-PI-5055 | VG | 5255 | 24VPHM | 24VPHM-PID-001/02 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Packing BH - EN 15848 | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-5271 | VG-5271 | 24VPHM-PI-5071 | VG | 5271 | 24VPHM | 24VPHM-PID-001/05 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Packing BH - EN 15848 | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-5281 | VG-5281 | 24VPHM-PI-5081 | VG | 5281 | 24VPHM | 24VPHM-PID-001/06 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Packing BH - EN 15848 | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | SC-2 SL2 | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VP00-VG-8015 | VG-8015 | 24VP00-PI-8015 | VG | 8015 | 24VP00 | 24VP00-PID-001/02 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | 0 | 1e-05 | Rate B - EN 12266 | Nitrogen Gas | 25 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8018 | VG-8018 | 24VP00-PI-8018 | VG | 8018 | 24VP00 | 24VP00-PID-001/02 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 40 | 1.5 | Packing BH - EN 15848 | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate B - EN 12266 | Water | 30 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VP00-VG-8019 | VG-8019 | 24VP00-PI-8019 | VG | 8019 | 24VP00 | 24VP00-PID-001/02 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 40 | 1.5 | Packing BH - EN 15848 | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate B - EN 12266 | Water | 30 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VP00-VG-8025 | VG-8025 | 24VP00-PI-8025 | VG | 8025 | 24VP00 | 24VP00-PID-001/03 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | 0 | 1e-05 | Rate B - EN 12266 | Nitrogen Gas | 25 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8028 | VG-8028 | 24VP00-PI-8028 | VG | 8028 | 24VP00 | 24VP00-PID-001/03 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 40 | 1.5 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate B - EN 12266 | Water | 30 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 905 | Passive
24VP00-VG-8029 | VG-8029 | 24VP00-PI-8029 | VG | 8029 | 24VP00 | 24VP00-PID-001/03 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 40 | 1.5 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate B - EN 12266 | Water | 30 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 905 | Passive
24VPHM-VG-8073 | VG-8073 | 24VPHM-PI-8074 | VG | 8073 | 24VPHM | 24VPHM-PID-001/05 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Bellows | 11-B2-01 | Fail Open | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Open during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | II | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 6 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 25 | 10000 | 20 | Red | Yellow | Red | On/Off | 7 | 7 | Yes | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-8080 | VG-8080 | 24VPHM-PI-8080 | VG | 8080 | 24VPHM | 24VPHM-PID-001/05 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Bellows | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | II | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 6 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 25 | 10000 | 20 | Red | Yellow | Red | On/Off | 7 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-8081 | VG-8081 | 24VPHM-PI-8581 | VG | 8081 | 24VPHM | 24VPHM-PID-001/06 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 50 | 2 | Bellows | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | I | 1e-05 | Rate C - EN 12266 | Water | 30 | 1 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 15 | 10000 | 20 | Red | Yellow | Red | On/Off | 2 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VP00-VG-8135 | VG-8135 | 24VP00-PI-8135 | VG | 8135 | 24VP00 | 24VP00-PID-001/04 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | 0 | 1e-05 | Rate B - EN 12266 | Nitrogen Gas | 25 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8138 | VG-8138 | 24VP00-PI-8138 | VG | 8138 | 24VP00 | 24VP00-PID-001/04 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 40 | 1.5 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate B - EN 12266 | Water | 30 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8139 | VG-8139 | 24VP00-PI-8139 | VG | 8139 | 24VP00 | 24VP00-PID-001/04 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 40 | 1.5 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate B - EN 12266 | Water | 30 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8145 | VG-8145 | 24VP00-PI-8145 | VG | 8145 | 24VP00 | 24VP00-PID-001/05 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | 0 | 1e-05 | Rate B - EN 12266 | Nitrogen Gas | 25 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8148 | VG-8148 | 24VP00-PI-8148 | VG | 8148 | 24VP00 | 24VP00-PID-001/05 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 40 | 1.5 | Packing BH - EN 15848 | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate B - EN 12266 | Water | 30 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VP00-VG-8149 | VG-8149 | 24VP00-PI-8149 | VG | 8149 | 24VP00 | 24VP00-PID-001/05 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 40 | 1.5 | Packing BH - EN 15848 | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate B - EN 12266 | Water | 30 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-8151 | VG-8151 | 24VPHM-PI-8051 | VG | 8151 | 24VPHM | 24VPHM-PID-001/02 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 50 | 2 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 15 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VPHM-VG-8170 | VG-8170 | 24VPHM-PI-8170 | VG | 8170 | 24VPHM | 24VPHM-PID-001/05 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 40 | 1.5 | Packing BH - EN 15848 | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-8173 | VG-8173 | 24VPHM-PI-8174 | VG | 8173 | 24VPHM | 24VPHM-PID-001/05 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 25 | 1 | Bellows | 11-B2-01 | Fail Open | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Open during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | II | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 6 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 25 | 10000 | 20 | Red | Yellow | Red | On/Off | 7 | 7 | Yes | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-8180 | VG-8180 | 24VPHM-PI-8180 | VG | 8180 | 24VPHM | 24VPHM-PID-001/06 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 40 | 1.5 | Packing BH - EN 15848 | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-8190 | VG-8190 | 24VPHM-PI-8190 | VG | 8190 | 24VPHM | 24VPHM-PID-001/07 | Pneumatic Globe Valve | Closed | Isolate | Pneumatic | Spring return | 40 | 1.5 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | On/Off | 8 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VPHM-VG-8373 | VG-8373 | 24VPHM-PI-8073 | VG | 8373 | 24VPHM | 24VPHM-PID-001/05 | Manual Globe Valve | Open | Isolate | Manual | N/A | 50 | 2 | Bellows | 11-B2-01 | N/A | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | TC-2A | N2 | N/A | II | I | 1e-05 | Rate C - EN 12266 | Water | 30 | 1 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 25 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open | 11-FS-01 | 142 | Passive
24VPHM-VG-8374 | VG-8374 | 24VPHM-PI-8574 | VG | 8374 | 24VPHM | 24VPHM-PID-001/05 | Manual Globe Valve | Closed | Isolate | Manual | N/A | 25 | 1 | Packing BH - EN 15848 | 11-B2-01 | N/A | Closed | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | TC-2A | N2 | N/A | I | 0 | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 60 | 0.75 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 700 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 142 | Passive
24VPHM-VG-8384 | VG-8384 | 24VPHM-PI-8074 | VG | 8384 | 24VPHM | 24VPHM-PID-001/04 | Manual Globe Valve | Open | Isolate | Manual | N/A | 25 | 1 | Bellows | 11-B1-01 | N/A | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | TC-2A | N2 | N/A | I | 0 | 1e-05 | Rate C - EN 12266 | Water | 60 | 8 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 5 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
24VPHM-VG-8385 | VG-8385 | 24VPHM-PI-8585 | VG | 8385 | 24VPHM | 24VPHM-PID-001/04 | Manual Globe Valve | Closed | Isolate | Manual | N/A | 25 | 1 | Packing BH - EN 15848 | 11-B2-01 | N/A | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | TC-2A | N2 | N/A | I | 0 | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 60 | 0.75 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 700 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 142
24VPHM-VG-8393 | VG-8393 | 24VPHM-PI-8593 | VG | 8393 | 24VPHM | 24VPHM-PID-001/07 | Manual Globe Valve | Closed | Isolate | Manual | N/A | 15 | 0.5 | Packing BH - EN 15848 | 11-B1-01 | N/A | LC | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | TC-2A | N2 | N/A | I | 0 | 1e-05 | Rate C - EN 12266 | Water | 11.7 | 0.75 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 1 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 277 | Passive
Note on BS2: Tallarigo Alberto: Passive: no need to keep hot/cold internal condition