## Sheet1
General data | [19 empty] | Materials |  |  |  | ITER Classification | [11 empty] | Leak requirements |  | Fluid parameters | [9 empty] | Environment |  |  |  |  | Actuator characteristics |  |  |  |  | PRV / RD characteristics |  |  |  | Check valves characteristics |  |  |  |  | I&C | Fire Protection
New Tag | Reference | New Line Number | Valve Code | Valve # | Scope/PBS | PID | Engineering Description | Valve position during normal operation | Function | Actuator type | Actuator Action | DN (in=out) [mm] | DN (in=out) [in] | Steam Seal Type | Room | Fail Position | Lock Position | Wedge/Disc Type | End Connection | Material - Body, Bonnet | Material - Stem, Ball, Disc, Plug | Material - Seat | Material Composition Requirement [Co, Nb, Ta] | Functional SIC classification | Train | PIC | Safety Function | QC | SC | VC | TC | ESPN | SIV | Fluid Group | PED | Tot Piping External Leak Tightness [Pa.m3.s-1] | Internal Leak Tightness | Fluid | Tope (deg) | Pope (bara) | Max Allowable Pressure PS (barg) | Pressure test (bar) | Td (deg) | Max Ambient T (deg) | Max Ambient P (bara) | ASME Class or PN, EN1092 | Nominal Flowrate (Nm3/h) | Neutron Flux (n/cm2.s) | Static Magnetic Field (mT) | Radiological zoning - Mode 0 | Radiological zoning - Mode 1 | Radiological zoning - Mode 2 | Actuator Control | Max DP Opening/Closing (bar) | Compressed Air supply (barg) | Mechanical Stop Yes/No | Required Stroke Time [s] [MIN, MAX] | Required relieving capacity (kg/h) | Set pressure (barg) | Atmospheric discharge | Superimposed backpressure (bar) | Check Valve Type | Min Closure time (s) | Max fluid deceleration (m/s2) | Max reverse fluid velocity (m/s) | Forward flow rate (m3/h) | Position indication | Fire Sectorization | Max Fire T (C) | Thermal Insulation Type
24VPHM-VG-1093 | VG-1093 | 24VPHM-PI-1093 | VG | 1093 | 24VPHM | 24VPHM-PID-001/08 | Pneumatic Butterfly Valve | Open | Isolate | Pneumatic | Spring return | 150 | 6 | Packing BH - EN 15848 | 11-L3-02E | Fail Close | N/A | Triple-Offset | Flanged | EN 1.4307, grade 304L | 304L | 304L | According to EN standard | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL3 | N/A | TC-2A | N/A | N/A | I | N/A | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 15 | 0.75 | 0.5 | 0.92391 | 80 | 130 | 1.2 | PN10 | 700 | 100000 | 125 | Red | Yellow | Red | On/Off | 1.75 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-04 | ISO 834 | Passive
24VPHM-VG-1193 | VG-1193 | 24VPHM-PI-1094 | VG | 1193 | 24VPHM | 24VPHM-PID-001/08 | Pneumatic Butterfly Valve | Open | Isolate | Pneumatic | Spring return | 150 | 6 | Packing BH - EN 15848 | 11-L3-02E | Fail Close | N/A | Triple-Offset | Flanged | EN 1.4307, grade 304L | 304L | 304L | According to EN standard | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL3 | N/A | TC-2A | N/A | N/A | I | N/A | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 15 | 0.75 | 0.5 | 0.92391 | 80 | 130 | 1.2 | PN10 | 700 | 100000 | 125 | Red | Yellow | Red | On/Off | 1.75 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-04 | ISO 834 | Passive
24VPHM-VG-1390 | VG-1390 | 24VPHM-PI-1090 | VG | 1390 | 24VPHM | 24VPHM-PID-001/08 | Manual Butterfly Valve | Closed | Isolate | No actuator | N/A | 150 | 6 | Packing BH - EN 15848 | 11-L3-02E | N/A | N/A | Triple-Offset | Flanged | EN 1.4307, grade 304L | 304L | 304L | According to EN standard | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | TC-2A | N/A | N/A | I | N/A | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 15 | 0.75 | 0.5 | 0.92391 | 80 | 130 | 1.2 | PN10 | 700 | 100000 | 125 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-04 | ISO 834 | Passive
24VPHM-VG-8091 | VG-8091 | 24VPHM-PI-8091 | VG | 8091 | 24VPHM | 24VPHM-PID-001/07 | Pneumatic Butterfly Valve | Open | Isolate | Pneumatic | Spring return | 150 | 6 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Triple-Offset | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N3 | YES | I | II | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 15 | 0.75 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 700 | 10000 | 20 | Red | Yellow | Red | On/Off | 1.75 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VPHM-VG-8092 | VG-8092 | 24VPHM-PI-8191 | VG | 8092 | 24VPHM | 24VPHM-PID-001/07 | Pneumatic Butterfly Valve | Open | Isolate | Pneumatic | Spring return | 150 | 6 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Triple-Offset | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N3 | YES | I | II | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 15 | 0.75 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 700 | 10000 | 20 | Red | Yellow | Red | On/Off | 1.75 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VPHM-VG-8191 | VG-8191 | 24VPHM-PI-8091 | VG | 8191 | 24VPHM | 24VPHM-PID-001/07 | Pneumatic Butterfly Valve | Open | Isolate | Pneumatic | Spring return | 150 | 6 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Triple-Offset | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N3 | YES | I | II | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 15 | 0.75 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 700 | 10000 | 20 | Red | Yellow | Red | On/Off | 1.75 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VPHM-VG-8192 | VG-8192 | 24VPHM-PI-8191 | VG | 8192 | 24VPHM | 24VPHM-PID-001/07 | Pneumatic Butterfly Valve | Open | Isolate | Pneumatic | Spring return | 150 | 6 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Triple-Offset | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N3 | YES | I | II | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 15 | 0.75 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 700 | 10000 | 20 | Red | Yellow | Red | On/Off | 1.75 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
Note on BS2: Tallarigo Alberto: Passive: no need to keep hot/cold internal condition