## Sheet1
General data | [19 empty] | Materials |  |  |  | ITER Classification | [11 empty] | Leak requirements |  | Fluid parameters | [9 empty] | Environment |  |  |  |  | Actuator characteristics |  |  |  |  | PRV / RD characteristics |  |  |  | Check valves characteristics |  |  |  |  | I&C | Fire Protection
New Tag | Reference | New Line Number | Valve Code | Valve # | Scope/PBS | PID | Engineering Description | Valve position during normal operation | Function | Actuator type | Actuator Action | DN (in=out) [mm] | DN (in=out) [in] | Steam Seal Type | Room | Fail Position | Lock Position | Wedge/Disc Type | End Connection | Material - Body, Bonnet | Material - Stem, Ball, Disc, Plug | Material - Seat | Material Composition Requirement [Co, Nb, Ta] | Functional SIC classification | Train | PIC | Safety Function | QC | SC | VC | TC | ESPN | SIV | Fluid Group | PED | Tot Piping External Leak Tightness [Pa.m3.s-1] | Internal Leak Tightness | Fluid | Tope (deg) | Pope (bara) | Max Allowable Pressure PS (barg) | Pressure test (bar) | Td (deg) | Max Ambient T (deg) | Max Ambient P (bara) | ASME Class or PN, EN1092 | Nominal Flowrate (Nm3/h) | Neutron Flux (n/cm2.s) | Static Magnetic Field (mT) | Radiological zoning - Mode 0 | Radiological zoning - Mode 1 | Radiological zoning - Mode 2 | Actuator Control | Max DP Opening/Closing (bar) | Compressed Air supply (barg) | Mechanical Stop Yes/No | Required Stroke Time [s] [MIN, MAX] | Required relieving capacity (kg/h) | Set pressure (barg) | Atmospheric discharge | Superimposed backpressure (bar) | Check Valve Type | Min Closure time (s) | Max fluid deceleration (m/s2) | Max reverse fluid velocity (m/s) | Forward flow rate (m3/h) | Position indication | Fire Sectorization | Max Fire T (C) | Thermal Insulation Type
24VPHM-VK-4301 | VK-4301 | 24VPHM-PI-4301 | VK | 4301 | 24VPHM | 24VPHM-PID-001/14 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 80 | 3 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | Non-SC | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 45 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Swing check | TBD | TBD | TBD | 45 | N/A | 11-FS-01 | 277 | Passive
24VP00-VK-4301 | VK-4301 | 24VP00-PI-4301 | VK | 4301 | 24VP00 | 24VP00-PID-001/07 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 80 | 3 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | Non-SC | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 45 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Swing check | TBD | TBD | TBD | 45 | N/A | 11-FS-01 | 277 | Passive
24VPHM-VK-4302 | VK-4302 | 24VPHM-PI-4309 | VK | 4302 | 24VPHM | 24VPHM-PID-001/14 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 15 | 0.5 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | Non-SC | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 6 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 1 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 1 | N/A | 11-FS-01 | 277 | Passive
24VPHM-VK-4303 | VK-4303 | 24VPHM-PI-4310 | VK | 4303 | 24VPHM | 24VPHM-PID-001/14 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 15 | 0.5 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | Non-SC | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 6 | 8 | 20 | 28.6 | 35 | 130 | 2 | PN25 | 1 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 1 | N/A | 11-FS-01 | 277 | Passive
24VP00-VK-4303 | VK-4303 | 24VP00-PI-4303 | VK | 4303 | 24VP00 | 24VP00-PID-001/07 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 15 | 0.5 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N/A | N/A | I | SEP | 1e-05 | Rate C - EN 12266 | Water | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 200 | N/A | 11-FS-01 | 277 | Passive
24VP00-VK-4313 | VK-4313 | 24VP00-PI-4313 | VK | 4313 | 24VP00 | 24VP00-PID-001/02 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 40 | 1.5 | N/A | 11-B2-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | N/A | N/A | QC-2 | Non-SC | N/A | N/A | N/A | N/A | II | SEP | N/A | Rate C - EN 12266 | Water | 30 | 7 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 10 | N/A | 11-FS-01 | 142 | Passive
24VP00-VK-8014 | VK-8014 | 24VP00-PI-8014 | VK | 8014 | 24VP00 | 24VP00-PID-001/02 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 200 | N/A | 11-FS-01 | 277 | Passive
24VP00-VK-8017 | VK-8017 | 24VP00-PI-8017 | VK | 8017 | 24VP00 | 24VP00-PID-001/02 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 200 | N/A | 11-FS-01 | 277 | Passive
24VP00-VK-8024 | VK-8024 | 24VP00-PI-8024 | VK | 8024 | 24VP00 | 24VP00-PID-001/03 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 200 | N/A | 11-FS-01 | 905 | Passive
24VP00-VK-8027 | VK-8027 | 24VP00-PI-8027 | VK | 8027 | 24VP00 | 24VP00-PID-001/03 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 200 | N/A | 11-FS-01 | 277 | Passive
24VP00-VK-8034 | VK-8034 | 24VP00-PI-8034 | VK | 8034 | 24VP00 | 24VP00-PID-001/04 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 200 | N/A | 11-FS-01 | 277 | Passive
24VP00-VK-8037 | VK-8037 | 24VP00-PI-8037 | VK | 8037 | 24VP00 | 24VP00-PID-001/04 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 200 | N/A | 11-FS-01 | 277 | Passive
24VP00-VK-8044 | VK-8044 | 24VP00-PI-8044 | VK | 8044 | 24VP00 | 24VP00-PID-001/05 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 200 | N/A | 11-FS-01 | 277 | Passive
24VP00-VK-8047 | VK-8047 | 24VP00-PI-8047 | VK | 8047 | 24VP00 | 24VP00-PID-001/05 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 200 | N/A | 11-FS-01 | 277 | Passive
24VPHM-VK-8073 | VK-8073 | 24VPHM-PI-8074 | VK | 8073 | 24VPHM | 24VPHM-PID-001/05 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B2-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | II | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 6 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 25 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 25 | N/A | 11-FS-01 | 142 | Passive
24VP00-VK-8114 | VK-8114 | 24VP00-PI-8114 | VK | 8114 | 24VP00 | 24VP00-PID-001/02 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 200 | N/A | 11-FS-01 | 277 | Passive
24VP00-VK-8117 | VK-8117 | 24VP00-PI-8117 | VK | 8117 | 24VP00 | 24VP00-PID-001/02 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 200 | N/A | 11-FS-01 | 277 | Passive
24VP00-VK-8124 | VK-8124 | 24VP00-PI-8124 | VK | 8124 | 24VP00 | 24VP00-PID-001/03 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 200 | N/A | 11-FS-01 | 905 | Passive
24VP00-VK-8127 | VK-8127 | 24VP00-PI-8127 | VK | 8127 | 24VP00 | 24VP00-PID-001/03 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 200 | N/A | 11-FS-01 | 277 | Passive
24VP00-VK-8134 | VK-8134 | 24VP00-PI-8134 | VK | 8134 | 24VP00 | 24VP00-PID-001/04 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 200 | N/A | 11-FS-01 | 277 | Passive
24VP00-VK-8137 | VK-8137 | 24VP00-PI-8137 | VK | 8137 | 24VP00 | 24VP00-PID-001/04 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 200 | N/A | 11-FS-01 | 277 | Passive
24VP00-VK-8144 | VK-8144 | 24VP00-PI-8144 | VK | 8144 | 24VP00 | 24VP00-PID-001/05 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 200 | N/A | 11-FS-01 | 277 | Passive
24VP00-VK-8147 | VK-8147 | 24VP00-PI-8147 | VK | 8147 | 24VP00 | 24VP00-PID-001/05 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 200 | N/A | 11-FS-01 | 277 | Passive
24VPHM-VK-8173 | VK-8173 | 24VPHM-PI-8174 | VK | 8173 | 24VPHM | 24VPHM-PID-001/05 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B2-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | II | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 6 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 25 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 25 | N/A | 11-FS-01 | 142 | Passive
24VP00-VK-8308 | VK-8308 | 24VP00-PI-8508 | VK | 8308 | 24VP00 | 24VP00-PID-001/09 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B2-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 5 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 5 | N/A | 11-FS-01 | 142 | Passive
24VP00-VK-8312 | VK-8312 | 24VP00-PI-8312 | VK | 8312 | 24VP00 | 24VP00-PID-001/10 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 40 | 1.5 | N/A | 11-B2-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 10 | N/A | 11-FS-01 | 142 | Passive
24VPHM-VK-8350 | VK-8350 | 24VPHM-PI-8050 | VK | 8350 | 24VPHM | 24VPHM-PID-001/02 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 80 | 3 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 SC-1 (S) SL3 | N/A | TC-2A | N2 | YES | I | II | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 230 | 1.15 | 20 | 41.2621 | 250 | 130 | 2 | PN40 | 300 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 300 | N/A | 11-FS-01 | 277 | Passive
24VPHM-VK-8352 | VK-8352 | 24VPHM-PI-8052 | VK | 8352 | 24VPHM | 24VPHM-PID-001/02 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 80 | 3 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | II | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 60 | 1 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 300 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 300 | N/A | 11-FS-01 | 277 | Passive
24VPHM-VK-8354 | VK-8354 | 24VPHM-PI-8054 | VK | 8354 | 24VPHM | 24VPHM-PID-001/02 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 1.5 | 15 | 27.7174 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 200 | N/A | 11-FS-01 | 142 | Passive
24VPHM-VK-8355 | VK-8355 | 24VPHM-PI-8055 | VK | 8355 | 24VPHM | 24VPHM-PID-001/02 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B2-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 200 | N/A | 11-FS-01 | 142 | Passive
24VPHM-VK-8356 | VK-8356 | 24VPHM-PI-8056 | VK | 8356 | 24VPHM | 24VPHM-PID-001/02 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 40 | 1.5 | N/A | 11-B2-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 10 | N/A | 11-FS-01 | 142 | Passive
24VPHM-VK-8359 | VK-8359 | 24VPHM-PI-8059 | VK | 8359 | 24VPHM | 24VPHM-PID-001/02 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 80 | 3 | N/A | 11-B1-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | II | 1e-05 | Rate C - EN 12266 | Air | 35 | 1 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 500 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 500 | N/A | 11-FS-01 | 142 | Passive
24VPHM-VK-8371 | VK-8371 | 24VPHM-PI-8071 | VK | 8371 | 24VPHM | 24VPHM-PID-001/05 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B2-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 200 | N/A | 11-FS-01 | 142 | Passive
24VPHM-VK-8372 | VK-8372 | 24VPHM-PI-8072 | VK | 8372 | 24VPHM | 24VPHM-PID-001/05 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 40 | 1.5 | N/A | 11-B2-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 10 | N/A | 11-FS-01 | 142 | Passive
24VPHM-VK-8380 | VK-8380 | 24VPHM-PI-8080 | VK | 8380 | 24VPHM | 24VPHM-PID-001/05 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B2-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | TC-2A | N2 | N/A | II | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 6 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 25 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 25 | N/A | 11-FS-01 | 142 | Passive
24VPHM-VK-8381 | VK-8381 | 24VPHM-PI-8081 | VK | 8381 | 24VPHM | 24VPHM-PID-001/06 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 25 | 1 | N/A | 11-B2-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 200 | N/A | 11-FS-01 | 142 | Passive
24VPHM-VK-8382 | VK-8382 | 24VPHM-PI-8082 | VK | 8382 | 24VPHM | 24VPHM-PID-001/06 | Non-Return Valve | Closed | Isolate | No actuator | N/A | 40 | 1.5 | N/A | 11-B2-01 | N/A | N/A | N/A | Flanged | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 7 | 20 | 36.9565 | 65 | 130 | 2 | PN25 | 10 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Lift check | TBD | TBD | TBD | 10 | N/A | 11-FS-01 | 142 | Passive
Note on BS2: Tallarigo Alberto: Passive: no need to keep hot/cold internal condition