## Sheet1
General data | [19 empty] | Materials |  |  |  | ITER Classification | [11 empty] | Leak requirements |  | Fluid parameters | [9 empty] | Environment |  |  |  |  | Actuator characteristics |  |  |  |  | PRV / RD characteristics |  |  |  | Check valves characteristics |  |  |  |  | I&C | Fire Protection
New Tag | Reference | New Line Number | Valve Code | Valve # | Scope/PBS | PID | Engineering Description | Valve position during normal operation | Function | Actuator type | Actuator Action | DN (in=out) [mm] | DN (in=out) [in] | Steam Seal Type | Room | Fail Position | Lock Position | Wedge/Disc Type | End Connection | Material - Body, Bonnet | Material - Stem, Ball, Disc, Plug | Material - Seat | Material Composition Requirement [Co, Nb, Ta] | Functional SIC classification | Train | PIC | Safety Function | QC | SC | VC | TC | ESPN | SIV | Fluid Group | PED | Tot Piping External Leak Tightness [Pa.m3.s-1] | Internal Leak Tightness | Fluid | Tope (deg) | Pope (bara) | Max Allowable Pressure PS (barg) | Pressure test (bar) | Td (deg) | Max Ambient T (deg) | Max Ambient P (bara) | ASME Class or PN, EN1092 | Nominal Flowrate (Nm3/h) | Neutron Flux (n/cm2.s) | Static Magnetic Field (mT) | Radiological zoning - Mode 0 | Radiological zoning - Mode 1 | Radiological zoning - Mode 2 | Actuator Control | Max DP Opening/Closing (bar) | Compressed Air supply (barg) | Mechanical Stop Yes/No | Required Stroke Time [s] [MIN, MAX] | Required relieving capacity (kg/h) | Set pressure (barg) | Atmospheric discharge | Superimposed backpressure (bar) | Check Valve Type | Min Closure time (s) | Max fluid deceleration (m/s2) | Max reverse fluid velocity (m/s) | Forward flow rate (m3/h) | Position indication | Fire Sectorization | Max Fire T (C) | Thermal Insulation Type
24VPHM-VG-1050 | VG-1050 | 24VPHM-PI-1050 | VG | 1050 | 24VPHM | 24VPHM-PID-001/02 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 80 | 3 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 SC-1 (S) SL3 | N/A | TC-2A | N/A | N/A | I | II | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 230 | 1.15 | 0.5 | 1.0316 | 250 | 130 | 2 | PN25 | 500 | 10000 | 20 | Red | Yellow | Red | On/Off | 2.15 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VPHM-VG-1059 | VG-1059 | 24VPHM-PI-1059 | VG | 1059 | 24VPHM | 24VPHM-PID-001/02 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 80 | 3 | Packing BH - EN 15848 | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | N/A | N/A | N/A | II | I | N/A | Rate C - EN 12266 | Air | 35 | 1 | 0.5 | 0.92391 | 125 | 130 | 2 | PN40 | 500 | 10000 | 20 | Red | Yellow | Red | On/Off | 2 | 7 | YES | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-1150 | VG-1150 | 24VPHM-PI-1150 | VG | 1150 | 24VPHM | 24VPHM-PID-001/02 | Pneumatic Gate Valve | Open | Isolate | Pneumatic | Spring return | 80 | 3 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 SC-1 (S) SL3 | N/A | TC-2A | N/A | N/A | I | II | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 230 | 1.15 | 0.5 | 1.0316 | 250 | 130 | 2 | PN25 | 500 | 10000 | 20 | Red | Yellow | Red | On/Off | 2.15 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VPHM-VG-1159 | VG-1159 | 24VPHM-PI-1159 | VG | 1159 | 24VPHM | 24VPHM-PID-001/02 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 80 | 3 | Packing BH - EN 15848 | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | N/A | N/A | N/A | II | I | N/A | Rate C - EN 12266 | Air | 35 | 1 | 0.5 | 0.92391 | 125 | 130 | 2 | PN40 | 500 | 10000 | 20 | Red | Yellow | Red | On/Off | 2 | 7 | YES | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VP00-VG-1224 | VG-1224 | 24VP00-PI-1524 | VG | 1224 | 24VP00 | 24VP00-PID-001/03 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 50 | 2 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | TC-2A | N/A | N/A | I | I | 1e-05 | Rate C - EN 12266 | Air | 40 | 0.8 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 1.8 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 905 | Passive
24VP00-VG-8010 | VG-8010 | 24VP00-PI-8512 | VG | 8010 | 24VP00 | 24VP00-PID-001/02 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 65 | 2.5 | Bellows | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | I | 1e-05 | Rate C - EN 12266 | Water | 30 | 1 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 25 | 10000 | 20 | Red | Yellow | Red | On/Off | 2 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VP00-VG-8011 | VG-8011 | 24VP00-PI-8511 | VG | 8011 | 24VP00 | 24VP00-PID-001/02 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 15 | 0.5 | Bellows | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 1 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 1 | 10000 | 20 | Red | Yellow | Red | On/Off | 2 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VP00-VG-8012 | VG-8012 | 24VP00-PI-8010 | VG | 8012 | 24VP00 | 24VP00-PID-001/02 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 100 | 4 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | A | PIC | Fully functional during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | II | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 40 | 2 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 5000 | 10000 | 20 | Red | Yellow | Red | On/Off | 3 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8013 | VG-8013 | 24VP00-PI-8013 | VG | 8013 | 24VP00 | 24VP00-PID-001/02 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 100 | 4 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | A | PIC | Fully functional during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | II | 1e-05 | Rate B - EN 12266 | Air, Steam, H2 | 40 | 0.934 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 300 | 10000 | 20 | Red | Yellow | Red | On/Off | 1.934 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8014 | VG-8014 | 24VP00-PI-8514 | VG | 8014 | 24VP00 | 24VP00-PID-001/02 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 50 | 2 | Packing BH - EN 15848 | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | I | 1e-05 | Rate B - EN 12266 | Air | 40 | 0.934 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 1.934 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VP00-VG-8020 | VG-8020 | 24VP00-PI-8522 | VG | 8020 | 24VP00 | 24VP00-PID-001/03 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 65 | 2.5 | Bellows | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 1 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 25 | 10000 | 20 | Red | Yellow | Red | On/Off | 2 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VP00-VG-8021 | VG-8021 | 24VP00-PI-8521 | VG | 8021 | 24VP00 | 24VP00-PID-001/03 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 15 | 0.5 | Bellows | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 1 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 1 | 10000 | 20 | Red | Yellow | Red | On/Off | 2 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8022 | VG-8022 | 24VP00-PI-8020 | VG | 8022 | 24VP00 | 24VP00-PID-001/03 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 100 | 4 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | A | PIC | Fully functional during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 40 | 2 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 5000 | 10000 | 20 | Red | Yellow | Red | On/Off | 3 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8023 | VG-8023 | 24VP00-PI-8023 | VG | 8023 | 24VP00 | 24VP00-PID-001/03 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 100 | 4 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | A | PIC | Fully functional during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | 0 | 1e-05 | Rate B - EN 12266 | Air, Steam, H2 | 40 | 0.934 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 300 | 10000 | 20 | Red | Yellow | Red | On/Off | 1.934 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8024 | VG-8024 | 24VP00-PI-8524 | VG | 8024 | 24VP00 | 24VP00-PID-001/03 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 50 | 2 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | 0 | 1e-05 | Rate B - EN 12266 | Air | 40 | 0.8 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 1.8 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 905 | Passive
24VP00-VG-8032 | VG-8032 | 24VP00-PI-8030 | VG | 8032 | 24VP00 | 24VP00-PID-001/04 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 100 | 4 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | A | PIC | Fully functional during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | II | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 40 | 2 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 5000 | 10000 | 20 | Red | Yellow | Red | On/Off | 3 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8033 | VG-8033 | 24VP00-PI-8033 | VG | 8033 | 24VP00 | 24VP00-PID-001/04 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 100 | 4 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | A | PIC | Fully functional during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | II | 1e-05 | Rate B - EN 12266 | Air, Steam, H2 | 40 | 0.934 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 300 | 10000 | 20 | Red | Yellow | Red | On/Off | 1.934 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8042 | VG-8042 | 24VP00-PI-8040 | VG | 8042 | 24VP00 | 24VP00-PID-001/05 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 100 | 4 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | A | PIC | Fully functional during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | II | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 40 | 2 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 5000 | 10000 | 20 | Red | Yellow | Red | On/Off | 3 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8043 | VG-8043 | 24VP00-PI-8043 | VG | 8043 | 24VP00 | 24VP00-PID-001/05 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 100 | 4 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | A | PIC | Fully functional during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | II | 1e-05 | Rate B - EN 12266 | Air, Steam, H2 | 40 | 0.934 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 300 | 10000 | 20 | Red | Yellow | Red | On/Off | 1.934 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VPHM-VG-8051 | VG-8051 | 24VPHM-PI-8551 | VG | 8051 | 24VPHM | 24VPHM-PID-001/02 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 65 | 2.5 | Bellows | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | II | 1e-05 | Rate C - EN 12266 | Water | 30 | 1 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 25 | 10000 | 20 | Red | Yellow | Red | On/Off | 2 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-8071 | VG-8071 | 24VPHM-PI-8571 | VG | 8071 | 24VPHM | 24VPHM-PID-001/05 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 65 | 2.5 | Bellows | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | II | 1e-05 | Rate C - EN 12266 | Water | 30 | 1 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 25 | 10000 | 20 | Red | Yellow | Red | On/Off | 2 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-8093 | VG-8093 | 24VPHM-PI-8093 | VG | 8093 | 24VPHM | 24VPHM-PID-001/07 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 50 | 2 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N3 | YES | I | I | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 1.5 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 50 | 10000 | 20 | Red | Yellow | Red | On/Off | 2.5 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 905 | Passive
24VPHM-VG-8094 | VG-8094 | 24VPHM-PI-8193 | VG | 8094 | 24VPHM | 24VPHM-PID-001/07 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 50 | 2 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | A | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N3 | YES | I | I | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 1.5 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 50 | 10000 | 20 | Red | Yellow | Red | On/Off | 2.5 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 905 | Passive
24VP00-VG-8112 | VG-8112 | 24VP00-PI-8110 | VG | 8112 | 24VP00 | 24VP00-PID-001/02 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 100 | 4 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | B | PIC | Fully functional during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | II | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 40 | 2 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 5000 | 10000 | 20 | Red | Yellow | Red | On/Off | 3 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8113 | VG-8113 | 24VP00-PI-8113 | VG | 8113 | 24VP00 | 24VP00-PID-001/02 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 100 | 4 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | B | PIC | Fully functional during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | II | 1e-05 | Rate B - EN 12266 | Air, Steam, H2 | 40 | 0.934 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 300 | 10000 | 20 | Red | Yellow | Red | On/Off | 1.934 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8122 | VG-8122 | 24VP00-PI-8120 | VG | 8122 | 24VP00 | 24VP00-PID-001/03 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 100 | 4 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | B | PIC | Fully functional during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | II | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 40 | 2 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 5000 | 10000 | 20 | Red | Yellow | Red | On/Off | 3 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8123 | VG-8123 | 24VP00-PI-8123 | VG | 8123 | 24VP00 | 24VP00-PID-001/03 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 100 | 4 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | B | PIC | Fully functional during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | II | 1e-05 | Rate B - EN 12266 | Air, Steam, H2 | 40 | 0.934 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 300 | 10000 | 20 | Red | Yellow | Red | On/Off | 1.934 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8130 | VG-8130 | 24VP00-PI-8532 | VG | 8130 | 24VP00 | 24VP00-PID-001/04 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 65 | 2.5 | Bellows | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | I | 1e-05 | Rate C - EN 12266 | Water | 30 | 1 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 25 | 10000 | 20 | Red | Yellow | Red | On/Off | 2 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VP00-VG-8131 | VG-8131 | 24VP00-PI-8531 | VG | 8131 | 24VP00 | 24VP00-PID-001/04 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 15 | 0.5 | Bellows | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 1 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 1 | 10000 | 20 | Red | Yellow | Red | On/Off | 2 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8132 | VG-8132 | 24VP00-PI-8130 | VG | 8132 | 24VP00 | 24VP00-PID-001/04 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 100 | 4 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | B | PIC | Fully functional during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | II | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 40 | 2 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 5000 | 10000 | 20 | Red | Yellow | Red | On/Off | 3 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8133 | VG-8133 | 24VP00-PI-8133 | VG | 8133 | 24VP00 | 24VP00-PID-001/04 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 100 | 4 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | B | PIC | Fully functional during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | II | 1e-05 | Rate B - EN 12266 | Air, Steam, H2 | 40 | 0.934 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 300 | 10000 | 20 | Red | Yellow | Red | On/Off | 1.934 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8134 | VG-8134 | 24VP00-PI-8534 | VG | 8134 | 24VP00 | 24VP00-PID-001/04 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 50 | 2 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | I | 1e-05 | Rate B - EN 12266 | Air | 40 | 0.934 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 1.934 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8140 | VG-8140 | 24VP00-PI-8542 | VG | 8140 | 24VP00 | 24VP00-PID-001/05 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 65 | 2.5 | Bellows | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | I | 1e-05 | Rate C - EN 12266 | Water | 30 | 1 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 25 | 10000 | 20 | Red | Yellow | Red | On/Off | 2 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VP00-VG-8141 | VG-8141 | 24VP00-PI-8541 | VG | 8141 | 24VP00 | 24VP00-PID-001/05 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 15 | 0.5 | Bellows | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 1 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 1 | 10000 | 20 | Red | Yellow | Red | On/Off | 2 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VP00-VG-8142 | VG-8142 | 24VP00-PI-8140 | VG | 8142 | 24VP00 | 24VP00-PID-001/05 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 100 | 4 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | B | PIC | Fully functional during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | II | 1e-05 | Rate C - EN 12266 | Air, Steam, H2 | 40 | 2 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 5000 | 10000 | 20 | Red | Yellow | Red | On/Off | 3 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8143 | VG-8143 | 24VP00-PI-8143 | VG | 8143 | 24VP00 | 24VP00-PID-001/05 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 100 | 4 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | B | PIC | Fully functional during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | N/A | I | II | 1e-05 | Rate B - EN 12266 | Air, Steam, H2 | 40 | 0.934 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 300 | 10000 | 20 | Red | Yellow | Red | On/Off | 1.934 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 277 | Passive
24VP00-VG-8144 | VG-8144 | 24VP00-PI-8544 | VG | 8144 | 24VP00 | 24VP00-PID-001/05 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 50 | 2 | Packing BH - EN 15848 | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-2 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N2 | YES | I | I | 1e-05 | Rate B - EN 12266 | Air | 40 | 0.934 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 200 | 10000 | 20 | Red | Yellow | Red | On/Off | 1.934 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-8193 | VG-8193 | 24VPHM-PI-8093 | VG | 8193 | 24VPHM | 24VPHM-PID-001/07 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 50 | 2 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N3 | YES | I | I | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 1.5 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 50 | 10000 | 20 | Red | Yellow | Red | On/Off | 2.5 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 905 | Passive
24VPHM-VG-8194 | VG-8194 | 24VPHM-PI-8193 | VG | 8194 | 24VPHM | 24VPHM-PID-001/07 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 50 | 2 | Packing BH - EN 15848 | 11-B1-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | SIC-1 | B | PIC | Closure during and after an accident | QC-1 | SC-1 (SF) SL2 | N/A | TC-2A | N3 | YES | I | I | 1e-05 | Rate C - EN 12266 | Nitrogen Gas | 25 | 1.5 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 50 | 10000 | 20 | Red | Yellow | Red | On/Off | 2.5 | 5.5 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 905 | Passive
24VP00-VG-8202 | VG-8202 | 24VP00-PI-8502 | VG | 8202 | 24VP00 | 24VP00-PID-001/09 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 15 | 0.5 | Bellows | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | TC-2A | N2 | N/A | I | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 10 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 5 | 10000 | 20 | Red | Yellow | Red | On/Off | 11 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VP00-VG-8242 | VG-8242 | 24VP00-PI-8542 | VG | 8242 | 24VP00 | 24VP00-PID-001/10 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 65 | 2.5 | Bellows | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | TC-2A | N2 | N/A | I | I | 1e-05 | Rate C - EN 12266 | Water | 30 | 1 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 25 | 10000 | 20 | Red | Yellow | Red | On/Off | 2 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-8252 | VG-8252 | 24VPHM-PI-8552 | VG | 8252 | 24VPHM | 24VPHM-PID-001/02 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 15 | 0.5 | Bellows | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | TC-2A | N2 | N/A | I | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 1 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 1 | 10000 | 20 | Red | Yellow | Red | On/Off | 2 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-8272 | VG-8272 | 24VPHM-PI-8572 | VG | 8272 | 24VPHM | 24VPHM-PID-001/05 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 15 | 0.5 | Bellows | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | TC-2A | N2 | N/A | I | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 1 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 1 | 10000 | 20 | Red | Yellow | Red | On/Off | 2 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-8282 | VG-8282 | 24VPHM-PI-8582 | VG | 8282 | 24VPHM | 24VPHM-PID-001/06 | Pneumatic Gate Valve | Closed | Isolate | Pneumatic | Spring return | 15 | 0.5 | Bellows | 11-B2-01 | Fail Close | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | TC-2A | N2 | N/A | I | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 1 | 15 | 27.7174 | 125 | 130 | 2 | PN25 | 1 | 10000 | 20 | Red | Yellow | Red | On/Off | 2 | 7 | N/A | Vendor to advise | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Limit Switch Open+Close | 11-FS-01 | 142 | Passive
24VPHM-VG-8391 | VG-8391 | 24VPHM-PI-8591 | VG | 8391 | 24VPHM | 24VPHM-PID-001/13 | Manual Gate Valve | Closed | Isolate | Manual | N/A | 15 | 0.5 | Bellows | 11-B2-01 | N/A | N/A | Vendor to advise | Welded | EN 1.4307, grade 304L | 304L | 304L | Co≤0.2%;Nb≤0.1%;Ta≤0.1%;B≤0.0018% | Non-SIC | N/A | PIC | Confinement during and after accidents | QC-1 | SC-1 (S) SL2 | N/A | TC-2A | N2 | N/A | II | 0 | 1e-05 | Rate C - EN 12266 | Water | 30 | 1 | 20 | 36.9565 | 125 | 130 | 2 | PN40 | 25 | 10000 | 20 | Red | Yellow | Red | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11-FS-01 | 142 | Passive
Note on BS2: Tallarigo Alberto: Passive: no need to keep hot/cold internal condition
Note on BE4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To limit the flow of Air into the system