## FLUID_DATA (hidden)
Absolute viscosity 1e-5 Pa s
Gases | Temperature degree C
| 0 | 20 | 50 | 100 | 200 | 300 | 400 | 500 | 600
Air | 1.73 | 1.82 | 1.96 | 2.2 | 2.61 | 2.98 | 3.32 | 3.64 | 3.94
Hydrogen | 0.84 | 0.88 | 0.94 | 1.04 | 1.21 | 1.37 | 1.53 | 1.69 | 1.84
Nitrogen | 1.66 | 1.76 | 1.89 | 2.12 | 2.51 | 2.86 | 3.19 | 3.49 | 3.78
Oxygen | 1.95 | 2.04 | 2.18 | 2.44 | 2.93 | 3.37 | 3.76 | 4.13 | 4.47
Steam | 0.92 | 0.97 | 1.06 | 1.24 | 1.62 | 2.03 | 2.45 | 2.86 | 3.26

## list
|  | VVPSS Temperature Measurement Datasheet | [7 empty] | Document Nº | BGR4R7
[10 empty] | Revision Nº | 1.2
[10 empty] | Page Nº | 1
1 | SCOPE | [8 empty] | SENSOR DATA (DIMENSIONS TO MATCH PARING THERMOWELL) | [7 empty] | PIPE / TANK DATA (THERMOWELL DESIGN & CLASSIFICATION TO BE ALIGNED ON PIPE / TANK) | [16 empty] | Wake Frequency limiting case for Thermowell sizing check |  |  |  |  | THERMOWELL (TW) DATA
2 | Sensor | Thermowell | Thermowell in procurement scope? | Room | Estmated absolute elevation (m) | Elevation in DTR (m) | PID | PID version | Connecting line / tank nozzle | Measurement description | Process Fluid | Sensor Safety Class | Sensor Quality Class | Recommended sensor type | Connecting port to thermowell | Sensor minimum temperature (℃) | Sensor maximum temperature (℃) | Pipe DN | Pipe/Tank Insul. Thick. (mm) | Pipe/tank wall Thick. (mm) | Pipe/Tank PS (barg) | Pipe/Tank TS (deg) | Pipe ID (mm) | Pipe class | Pipe Schedule | Pipe/Tank Safety Class | Pipe/Tank Quality Class | Pipe/Tank Seismic class | Pipe/Tank Vacuum class | Pipe/Tank tritium class | Pipe/Tank ESPN | PED Fluid group | PSxDN | PED Category | Temperature (℃) | Pressure (kPa) | Maximum Flow (Nm3/h gas or m3/h liquid) | Fluid density (kg/m3) | Fluid Viscosity (kg/m/s) | TW shank type | Instrument connection thread depth (mm) | TW extension - straight length (mm) | TW immersion - tapered length (mm) | TW root diameter (mm) | TW tip diameter (mm) | TW bore diameter (mm) | TW tip tick. (mm)
3 | 24VP00-MTE-1213 | 24VP00-MTW-1213 | YES | 11-B2-01 | -13.09 | 0 | 24VP00-PID-001/02 | G | 24VP00-PI-1311 | SLT cooling loop temperature | Chilled water | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPTM | 0 | 35 | 80 | 25 | 7.62 | 15 | 125 | 77.92 | # 300 | 80S | Non-SIC | QC-3 | SC-1 (S) SL2 | VQC-NA | N/A | N/A | 2 | 1200 | SEP | 35 | 100 | 25 | 1000 | 0.00131 | tapered | 25 | 35 | 65 | 25.4 | 16 | 6.6 | 6.4
4 | 24VPHM-MTE-8171 | 24VPHM-MTW-8171 | NO | 11-B2-01 | -12.253 | 0.8 | 24VPHM-PID-001/05 | F | QEN T01 | Quencher water temperature | Tritiated water | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPTM | 6 | 100 | N/A | 50 | 25 | 20 | 130 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1-S (SL-3) | N/A | TC2A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 25 | 200 | 150 | 25.4 | 16 | 7 | 3
5 | 24VPHM-MTE-8281 | 24VPHM-MTW-8281 | NO | 11-B2-01 | -12.218 | 0.9 | 24VPHM-PID-001/06 | F | OFT T02 | OFT water temperature | Tritiated water | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPTM | 6 | 100 | N/A | 50 | 25 | 20 | 130 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1-S | N/A | TC2A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 25 | 200 | 150 | 25.4 | 16 | 7 | 5
6 | 24VP00-MTH-8011 | 24VP00-MTW-8011 | NO | 11-B2-01 | -10.622 | 2.5 | 24VP00-PID-001/02 | G | SLT N03.1 | SLT water temperature | Tritiated water | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
7 | 24VP00-MTH-8014 | 24VP00-MTW-8014 | NO | 11-B2-01 | -10.622 | 2.5 | 24VP00-PID-001/02 | G | SLT N05.1 | SLT water temperature | Tritiated water | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
8 | 24VP00-MTH-8041 | 24VP00-MTW-8041 | NO | 11-B2-01 | -10.622 | 2.5 | 24VP00-PID-001/05 | G | LLT3-N03.1 | LLT-3 water temperature | Tritiated water | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
9 | 24VP00-MTH-8044 | 24VP00-MTW-8044 | NO | 11-B2-01 | -10.622 | 2.5 | 24VP00-PID-001/05 | G | LLT3-N05.1 | LLT-3 water temperature | Tritiated water | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
10 | 24VP00-MTH-8111 | 24VP00-MTW-8111 | NO | 11-B2-01 | -10.622 | 2.5 | 24VP00-PID-001/02 | G | SLT N03.2 | SLT water temperature | Tritiated water | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
11 | 24VP00-MTH-8114 | 24VP00-MTW-8114 | NO | 11-B2-01 | -10.622 | 2.5 | 24VP00-PID-001/02 | G | SLT N05.2 | SLT water temperature | Tritiated water | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
12 | 24VP00-MTH-8141 | 24VP00-MTW-8141 | NO | 11-B2-01 | -10.622 | 2.5 | 24VP00-PID-001/05 | G | LLT3-N03.2 | LLT-3 water temperature | Tritiated water | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
13 | 24VP00-MTH-8144 | 24VP00-MTW-8144 | NO | 11-B2-01 | -10.622 | 2.5 | 24VP00-PID-001/05 | G | LLT3-N05.2 | LLT-3 water temperature | Tritiated water | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
14 | 24VP00-MTE-8215 | 24VP00-MTW-8215 | NO | 11-B2-01 | -10.622 | 2.5 | 24VP00-PID-001/02 | G | SLT N06 | SLT water temperature | Tritiated water | SIC-2 | QC-2 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
15 | 24VP00-MTE-8216 | 24VP00-MTW-8216 | NO | 11-B2-01 | -10.622 | 2.5 | 24VP00-PID-001/02 | G | SLT N04 | SLT water temperature | Tritiated water | SIC-2 | QC-2 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
16 | 24VP00-MTE-8245 | 24VP00-MTW-8245 | NO | 11-B2-01 | -10.622 | 2.5 | 24VP00-PID-001/05 | G | LLT2-N06 | LLT-3 water temperature | Tritiated water | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
17 | 24VP00-MTE-8246 | 24VP00-MTW-8246 | NO | 11-B2-01 | -10.622 | 2.5 | 24VP00-PID-001/05 | G | LLT2-N04 | LLT-3 water temperature | Tritiated water | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
18 | 24VPHM-MTH-8051 | 24VPHM-MTW-8051 | NO | 11-B2-01 | -9.897 | 3.2 | 24VPHM-PID-001/02 | F | PST T04 | PST water temperature | Tritiated water | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPTM | 6 | 100 | N/A |  | 25 | 20 | 130 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1-S (SL-3) | N/A | TC2A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 25 | 200 | 150 | 25.4 | 16 | 7 | 5
19 | 24VPHM-MTH-8151 | 24VPHM-MTW-8151 | NO | 11-B2-01 | -9.897 | 3.2 | 24VPHM-PID-001/02 | F | PST T03 | PST water temperature | Tritiated water | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPTM | 6 | 100 | N/A |  | 25 | 20 | 130 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1-S (SL-3) | N/A | TC2A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 25 | 200 | 150 | 25.4 | 16 | 7 | 5
20 | 24VPHM-MTE-8251 | 24VPHM-MTW-8251 | NO | 11-B2-01 | -9.897 | 3.2 | 24VPHM-PID-001/02 | F | PST T01 | PST water temperature | Tritiated water | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPTM | 6 | 100 | N/A |  | 25 | 20 | 130 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1-S (SL-3) | N/A | TC2A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 25 | 200 | 150 | 25.4 | 16 | 7 | 5
21 | 24VPHM-MTE-8282 | 24VPHM-MTW-8282 | NO | 11-B2-01 | -9.5 | 3.6 | 24VPHM-PID-001/06 | F | OFT T01 | OFT gas temperature | Air/steam/H2 | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPTM | 6 | 100 | N/A | 50 | 25 | 20 | 130 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1-S | N/A | TC2A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 25 | 200 | 150 | 25.4 | 16 | 7 | 5
22 | 24VPHM-MTE-8071 | 24VPHM-MTW-8071 | NO | 11-B2-01 | -8.87 | 4.2 | 24VPHM-PID-001/05 | F | QEN T02 | Quencher gas temperature | Air/steam/H2 | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPTM | 6 | 100 | N/A | 50 | 25 | 20 | 130 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1-S (SL-3) | N/A | TC2A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 25 | 200 | 150 | 25.4 | 16 | 7 | 5
23 | 24VP00-MTE-8217 | 24VP00-MTW-8217 | NO | 11-B2-01 | -8.2 | 4.9 | 24VP00-PID-001/02 | G | SLT N16 | SLT gas temperature | Air/steam/H2 | SIC-2 | QC-2 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 125 | N/A | 50 | 72 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
24 | 24VP00-MTE-8218 | 24VP00-MTW-8218 | NO | 11-B2-01 | -8.2 | 4.9 | 24VP00-PID-001/02 | G | SLT N19 | SLT gas temperature | Air/steam/H2 | SIC-2 | QC-2 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 125 | N/A | 50 | 72 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
25 | 24VP00-MTE-8247 | 24VP00-MTW-8247 | NO | 11-B2-01 | -8.2 | 4.9 | 24VP00-PID-001/05 | G | LLT3-N16 | LLT-3 gas temperature | Air/steam/H2 | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 125 | N/A | 50 | 72 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
26 | 24VP00-MTE-8248 | 24VP00-MTW-8248 | NO | 11-B2-01 | -8.2 | 4.9 | 24VP00-PID-001/05 | G | LLT3-N19 | LLT-3 gas temperature | Air/steam/H2 | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 125 | N/A | 50 | 72 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
27 | 24VPHM-MTE-3200 | 24VPHM-MTW-3200 | YES | 11-B1-01 | -7.87 | 5.2 | 24VPHM-PID-001/11 | F | 24VPHM-PI-3001 | CHH1 Train-A inlet temperature | Chilled water | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPTM | 0 | 35 | 80 | 50 | 7.62 | 20 | 35 | 77.92 | # 300 | 80S | SIC-2 | QC-2 | SC-1 (S) SL2 | VQC-NA | N/A | N/A | 2 | 1600 | SEP | 35 | 600 | 25 | 1000 | 0.00131 | tapered | 25 | 60 | 65 | 25.4 | 16 | 6.6 | 6.4
28 | 24VPHM-MTE-3240 | 24VPHM-MTW-3240 | YES | 11-B1-01 | -7.87 | 5.2 | 24VPHM-PID-001/11 | F | 24VPHM-PI-3003 | CHH1 Train-A outlet temperature | Chilled water | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPTM | 0 | 35 | 80 | 50 | 7.62 | 20 | 35 | 77.92 | # 300 | 80S | SIC-2 | QC-2 | SC-1 (S) SL2 | VQC-NA | N/A | N/A | 2 | 1600 | SEP | 35 | 600 | 25 | 1000 | 0.00131 | tapered | 25 | 60 | 65 | 25.4 | 16 | 6.6 | 6.4
29 | 24VPHM-MTE-8060 | 24VPHM-MTW-8060 | YES | 11-B2-01 | -7.76 | 5.3 | 24VPHM-PID-001/03 | F | 24VPHM-PI-8061 | Recombiner heater outlet temperature | Air/steam/H2 | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPTM | 6 | 100 | 150 | 50 | 10.97 | 20 | 125 | 146.36 | # 300 | 80S | SIC-1 | QC-1 | SC-1 (S) SL2 | VQC-NA | TC-2A | N2 | 1 | 3000 | II | 100 | 70 | 600 | 0.623 | 2.14e-05 | tapered | 25 | 65 | 90 | 25.4 | 16 | 6.6 | 6.4
30 | 24VPHM-MTE-8160 | 24VPHM-MTW-8160 | YES | 11-B2-01 | -7.76 | 5.3 | 24VPHM-PID-001/03 | F | 24VPHM-PI-8061 | Recombiner heater outlet temperature | Air/steam/H2 | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPTM | 6 | 100 | 150 | 50 | 10.97 | 20 | 125 | 146.36 | # 300 | 80S | SIC-1 | QC-1 | SC-1 (S) SL2 | VQC-NA | TC-2A | N2 | 1 | 3000 | II | 100 | 70 | 600 | 0.623 | 2.14e-05 | tapered | 25 | 65 | 90 | 25.4 | 16 | 6.6 | 6.4
31 | 24VPHM-MTE-8253 | 24VPHM-MTW-8253 | NO | 11-B2-01 | -7.45 | 5.6 | 24VPHM-PID-001/02 | F | PST T02 | PST gas temperature | Air/steam/H2 | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPTM | 6 | 100 | N/A | 50 | 25 | 20 | 130 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1-S (SL-3) | N/A | TC2A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 25 | 200 | 150 | 25.4 | 16 | 7 | 5
32 | 24VPHM-MTE-1058 | 24VPHM-MTW-1058 | YES | 11-B1-01 | -5.89 | 7.2 | 24VPHM-PID-001/02 | F | 24VPHM-PI-1059 | Air supply from DTR to HMS Temperature | Air | SIC-1 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPTM | 18 | 35 | 80 | 50 | 7.62 | 20 | 125 | 77.92 | # 300 | 80S | SIC-1 | QC-1 | SC-1 (S) SL2 | VQC-NA | TC-2A | N/A | 2 | 1600 | I | 35 | 90 | 385 | 1.018 | 1.82e-05 | tapered | 25 | 60 | 65 | 25.4 | 16 | 6.6 | 6.4
33 | 24VPHM-MTE-1059 | 24VPHM-MTW-1059 | YES | 11-B1-01 | -5.89 | 7.2 | 24VPHM-PID-001/02 | F | 24VPHM-PI-1059 | Air supply from DTR to HMS Temperature | Air | SIC-1 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPTM | 18 | 35 | 80 | 50 | 7.62 | 20 | 125 | 77.92 | # 300 | 80S | SIC-1 | QC-1 | SC-1 (S) SL2 | VQC-NA | TC-2A | N/A | 2 | 1600 | I | 35 | 90 | 385 | 1.018 | 1.82e-05 | tapered | 25 | 60 | 65 | 25.4 | 16 | 6.6 | 6.4
34 | 24VPHM-MTE-1158 | 24VPHM-MTW-1158 | YES | 11-B1-01 | -5.89 | 7.2 | 24VPHM-PID-001/02 | F | 24VPHM-PI-1059 | Air supply from DTR to HMS Temperature | Air | SIC-1 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPTM | 18 | 35 | 80 | 50 | 7.62 | 20 | 125 | 77.92 | # 300 | 80S | SIC-1 | QC-1 | SC-1 (S) SL2 | VQC-NA | TC-2A | N/A | 2 | 1600 | I | 35 | 90 | 385 | 1.018 | 1.82e-05 | tapered | 25 | 60 | 65 | 25.4 | 16 | 6.6 | 6.4
35 | 24VPHM-MTE-1159 | 24VPHM-MTW-1159 | YES | 11-B1-01 | -5.89 | 7.2 | 24VPHM-PID-001/02 | F | 24VPHM-PI-1059 | Air supply from DTR to HMS Temperature | Air | SIC-1 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPTM | 18 | 35 | 80 | 50 | 7.62 | 20 | 125 | 77.92 | # 300 | 80S | SIC-1 | QC-1 | SC-1 (S) SL2 | VQC-NA | TC-2A | N/A | 2 | 1600 | I | 35 | 90 | 385 | 1.018 | 1.82e-05 | tapered | 25 | 60 | 65 | 25.4 | 16 | 6.6 | 6.4
36 | 24VPHM-MTE-3020 | 24VPHM-MTW-3020 | YES | 11-B1-01 | -5.77 | 7.3 | 24VPHM-PID-001/07 | F | 24VPHM-PI-3002 | Chilled water outlet EXC train A temp. | Chilled water | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPTM | 0 | 35 | 80 | 50 | 7.62 | 20 | 35 | 77.92 | # 300 | 80S | SIC-2 | QC-2 | SC-1 (S) SL2 | VQC-NA | N/A | N/A | 2 | 1600 | SEP | 35 | 600 | 25 | 1000 | 0.00131 | tapered | 25 | 60 | 65 | 25.4 | 16 | 6.6 | 6.4
37 | 24VP00-MTH-8021 | 24VP00-MTW-8021 | NO | 11-B1-01 | -5.84 | 7.3 | 24VP00-PID-001/03 | G | LLT1-N03.1 | LLT-1 water temperature | Tritiated water | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
38 | 24VP00-MTH-8024 | 24VP00-MTW-8024 | NO | 11-B1-01 | -5.84 | 7.3 | 24VP00-PID-001/03 | G | LLT1-N05.1 | LLT-1 water temperature | Tritiated water | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
39 | 24VP00-MTH-8031 | 24VP00-MTW-8031 | NO | 11-B1-01 | -5.84 | 7.3 | 24VP00-PID-001/04 | G | LLT2-N03.1 | LLT-2 water temperature | Tritiated water | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
40 | 24VP00-MTH-8034 | 24VP00-MTW-8034 | NO | 11-B1-01 | -5.84 | 7.3 | 24VP00-PID-001/04 | G | LLT2-N05.1 | LLT-2 water temperature | Tritiated water | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
41 | 24VP00-MTH-8121 | 24VP00-MTW-8121 | NO | 11-B1-01 | -5.84 | 7.3 | 24VP00-PID-001/03 | G | LLT1-N03.2 | LLT-1 water temperature | Tritiated water | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
42 | 24VP00-MTH-8124 | 24VP00-MTW-8124 | NO | 11-B1-01 | -5.84 | 7.3 | 24VP00-PID-001/03 | G | LLT1-N05.2 | LLT-1 water temperature | Tritiated water | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
43 | 24VP00-MTH-8131 | 24VP00-MTW-8131 | NO | 11-B1-01 | -5.84 | 7.3 | 24VP00-PID-001/04 | G | LLT2-N03.2 | LLT-2 water temperature | Tritiated water | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
44 | 24VP00-MTH-8134 | 24VP00-MTW-8134 | NO | 11-B1-01 | -5.84 | 7.3 | 24VP00-PID-001/04 | G | LLT2-N05.2 | LLT-2 water temperature | Tritiated water | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
45 | 24VP00-MTE-8225 | 24VP00-MTW-8225 | NO | 11-B1-01 | -5.84 | 7.3 | 24VP00-PID-001/03 | G | LLT1-N06 | LLT-1 water temperature | Tritiated water | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
46 | 24VP00-MTE-8226 | 24VP00-MTW-8226 | NO | 11-B1-01 | -5.84 | 7.3 | 24VP00-PID-001/03 | G | LLT1-N04 | LLT-1 water temperature | Tritiated water | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
47 | 24VP00-MTE-8235 | 24VP00-MTW-8235 | NO | 11-B1-01 | -5.84 | 7.3 | 24VP00-PID-001/04 | G | LLT2-N06 | LLT-2 water temperature | Tritiated water | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
48 | 24VP00-MTE-8236 | 24VP00-MTW-8236 | NO | 11-B1-01 | -5.84 | 7.3 | 24VP00-PID-001/04 | G | LLT2-N04 | LLT-2 water temperature | Tritiated water | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 100 | N/A | 50 | 65 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
49 | 24VPHM-MTE-3120 | 24VPHM-MTW-3120 | YES | 11-B1-01 | -5.2 | 7.9 | 24VPHM-PID-001/07 | F | 24VPHM-PI-3102 | Chilled water outlet EXC train B temp. | Chilled water | SIC-2 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPTM | 0 | 35 | 80 | 50 | 7.62 | 20 | 35 | 77.92 | # 300 | 80S | SIC-2 | QC-2 | SC-1 (S) SL2 | VQC-NA | N/A | N/A | 2 | 1600 | SEP | 35 | 600 | 25 | 1000 | 0.00131 | tapered | 25 | 60 | 65 | 25.4 | 16 | 6.6 | 6.4
50 | 24VPHM-MTH-8191 | 24VPHM-MTW-8091 | YES | 11-B1-01 | -4.875 | 8.2 | 24VPHM-PID-001/07 | F | 24VPHM-PI-8091 | Exhaust gas outlet EXC temp. | Air/steam/H2 | SIC-1 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPTM | 6 | 60 | 150 | 50 | 10.97 | 20 | 125 | 146.36 | # 300 | 80S | SIC-1 | QC-1 | SC-1 (S) SL2 | VQC-NA | TC-2A | N2 | 1 | 3000 | II | 6 | 115 | 600 | 1.369 | 1.69e-05 | tapered | 25 | 65 | 90 | 25.4 | 16 | 6.6 | 6.4
51 | 24VPHM-MTE-8092 | 24VPHM-MTW-8092 | YES | 11-B1-01 | -4.875 | 8.2 | 24VPHM-PID-001/07 | F | 24VPHM-PI-8091 | Exhaust gas outlet EXC temp. | Air/steam/H2 | SIC-1 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPTM | 6 | 60 | 150 | 50 | 10.97 | 20 | 125 | 146.36 | # 300 | 80S | SIC-1 | QC-1 | SC-1 (S) SL2 | VQC-NA | TC-2A | N2 | 1 | 3000 | II | 6 | 115 | 600 | 1.369 | 1.69e-05 | tapered | 25 | 65 | 90 | 25.4 | 16 | 6.6 | 6.4
52 | 24VPHM-MTH-8091 | 24VPHM-MTW-8191 | YES | 11-B1-01 | -4.875 | 8.2 | 24VPHM-PID-001/07 | F | 24VPHM-PI-8091 | Exhaust gas outlet EXC temp. | Air/steam/H2 | SIC-1 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPTM | 6 | 60 | 150 | 50 | 10.97 | 20 | 125 | 146.36 | # 300 | 80S | SIC-1 | QC-1 | SC-1 (S) SL2 | VQC-NA | TC-2A | N2 | 1 | 3000 | II | 6 | 115 | 600 | 1.369 | 1.69e-05 | tapered | 25 | 65 | 90 | 25.4 | 16 | 6.6 | 6.4
53 | 24VPHM-MTE-8192 | 24VPHM-MTW-8192 | YES | 11-B1-01 | -4.875 | 8.2 | 24VPHM-PID-001/07 | F | 24VPHM-PI-8091 | Exhaust gas outlet EXC temp. | Air/steam/H2 | SIC-1 | QC-1 | 4-Wire RTD PT-100 | 1/2 NPTM | 6 | 60 | 150 | 50 | 10.97 | 20 | 125 | 146.36 | # 300 | 80S | SIC-1 | QC-1 | SC-1 (S) SL2 | VQC-NA | TC-2A | N2 | 1 | 3000 | II | 6 | 115 | 600 | 1.369 | 1.69e-05 | tapered | 25 | 65 | 90 | 25.4 | 16 | 6.6 | 6.4
54 | 24VPHM-MTE-8162 | 24VPHM-MTW-8162 | NO | 11-B1-01 | -4.45 | 8.6 | 24VPHM-PID-001/03 | F | Recombiner heater T4 | Recombiner heater gas temperature | Air/steam/H2 | SIC-2 | QC-1 | 4-Wire RTD PT-100 | to be confirmed | 6 | 100 | N/A | to be confirmed | to be confirmed | 20 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1-S (SL-3) | N/A | TC2A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | to be confirmed | to be confirmed | to be confirmed | to be confirmed | to be confirmed | to be confirmed | to be confirmed | to be confirmed
55 | 24VPHM-MTE-8072 | N/A surface temperature | N/A | 11-B1-01 | -4.45 | 8.6 | 24VPHM-PID-001/04 | F | Annular recombiner | Annular recombiner surface temperature | Air/steam/H2 | SIC-2 | QC-1 | Surface 4-Wire RTD To be confirmed | N/A | 6 | 400 | N/A | to be confirmed | to be confirmed | 20 | 300 | N/A | N/A | N/A | SIC-1 | QC-2 | SC1-S (SL-3) | N/A | TC2A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
56 | 24VPHM-MTE-8172 | N/A surface temperature | N/A | 11-B1-01 | -4.45 | 8.6 | 24VPHM-PID-001/04 | F | Annular recombiner | Annular recombiner surface temperature | Air/steam/H2 | SIC-2 | QC-1 | Surface 4-Wire RTD To be confirmed | N/A | 6 | 400 | N/A | to be confirmed | to be confirmed | 20 | 300 | N/A | N/A | N/A | SIC-1 | QC-2 | SC1-S (SL-3) | N/A | TC2A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
57 | 24VPHM-MTE-8080 | N/A surface temperature | N/A | 11-B1-01 | -4.45 | 8.6 | 24VPHM-PID-001/16 | F | Series recombiner | Series recombiner surface temperature | Air/steam/H2 | SIC-2 | QC-1 | Surface 4-Wire RTD To be confirmed | N/A | 6 | 400 | N/A | to be confirmed | to be confirmed | 20 | 300 | N/A | N/A | N/A | SIC-1 | QC-2 | SC1-S (SL-3) | N/A | TC2A | N2 | 1 | N/A | IV | [5 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A
58 | 24VPHM-MTE-8180 | N/A surface temperature | N/A | 11-B1-01 | -4.45 | 8.6 | 24VPHM-PID-001/16 | F | Series recombiner | Series recombiner surface temperature | Air/steam/H2 | SIC-2 | QC-1 | Surface 4-Wire RTD To be confirmed | N/A | 6 | 400 | N/A | to be confirmed | to be confirmed | 20 | 300 | N/A | N/A | N/A | SIC-1 | QC-2 | SC1-S (SL-3) | N/A | TC2A | N2 | 1 | N/A | IV | [5 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A
59 | 24VPHM-MTE-8061 | 24VPHM-MTW-8061 | NO | 11-B1-01 | -4.45 | 8.6 | 24VPHM-PID-001/03 | F | Recombiner heater T1 | Recombiner heater gas temperature | Air/steam/H2 | SIC-2 | QC-1 | 4-Wire RTD PT-100 | to be confirmed | 6 | 100 | N/A | to be confirmed | to be confirmed | 20 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1-S (SL-3) | N/A | TC2A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | to be confirmed | to be confirmed | to be confirmed | to be confirmed | to be confirmed | to be confirmed | to be confirmed | to be confirmed
60 | 24VPHM-MTE-8062 | 24VPHM-MTW-8062 | NO | 11-B1-01 | -4.45 | 8.6 | 24VPHM-PID-001/03 | F | Recombiner heater T2 | Recombiner heater gas temperature | Air/steam/H2 | SIC-2 | QC-1 | 4-Wire RTD PT-100 | to be confirmed | 6 | 100 | N/A | to be confirmed | to be confirmed | 20 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1-S (SL-3) | N/A | TC2A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | to be confirmed | to be confirmed | to be confirmed | to be confirmed | to be confirmed | to be confirmed | to be confirmed | to be confirmed
61 | 24VPHM-MTE-8161 | 24VPHM-MTW-8161 | NO | 11-B1-01 | -4.45 | 8.6 | 24VPHM-PID-001/03 | F | Recombiner heater T3 | Recombiner heater gas temperature | Air/steam/H2 | SIC-2 | QC-1 | 4-Wire RTD PT-100 | to be confirmed | 6 | 100 | N/A | to be confirmed | to be confirmed | 20 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1-S (SL-3) | N/A | TC2A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | to be confirmed | to be confirmed | to be confirmed | to be confirmed | to be confirmed | to be confirmed | to be confirmed | to be confirmed
62 | 24VPHM-MTE-1250 | 24VPHM-MTW-1250 | YES | 11-B1-01 | -4.44 | 8.7 | 24VPHM-PID-001/02 | F | 24VPHM-PI-1050 | SLT bypass temperature | Air/steam/H2 | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPTM | 18 | 230 | 80 | 50 | 7.62 | 15 | 250 | 77.92 | # 300 | 80S | SIC-1 | QC-1 | SC-1 (S) SL3 | VQC-2A | TC-2A | N/A | 1 | 1200 | II | 100 | 87 | 350 | 0.493 | 1.23e-05 | tapered | 25 | 60 | 65 | 25.4 | 16 | 6.6 | 6.4
63 | 24VPHM-MTE-3201 | 24VPHM-MTW-3201 | YES | 11-B1-01 | -4.22 | 8.9 | 24VPHM-PID-001/11 | F | 24VPHM-PI-3101 | CHH1 Train-B inlet temperature | Chilled water | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPTM | 0 | 35 | 80 | 50 | 7.62 | 20 | 35 | 77.92 | # 300 | 80S | SIC-2 | QC-2 | SC-1 (S) SL2 | VQC-NA | N/A | N/A | 2 | 1600 | SEP | 35 | 600 | 25 | 1000 | 0.00131 | tapered | 25 | 60 | 65 | 25.4 | 16 | 6.6 | 6.4
64 | 24VPHM-MTE-8283 | 24VPHM-MTW-8283 | YES | 11-B1-01 | -4.15 | 8.9 | 24VPHM-PID-001/07 | F | 24VPHM-PI-8087 | Exhaust gas inlet EXC temp. | Air/steam/H2 | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPTM | 6 | 60 | 150 | 50 | 10.97 | 20 | 125 | 146.36 | # 300 | 80S | SIC-1 | QC-1 | SC-1 (S) SL2 | VQC-NA | TC-2A | N2 | 1 | 3000 | II | 6 | 115 | 600 | 1.369 | 1.69e-05 | tapered | 25 | 65 | 90 | 25.4 | 16 | 6.6 | 6.4
65 | 24VPHM-MTE-3241 | 24VPHM-MTW-3241 | YES | 11-B1-01 | -3.78 | 9.3 | 24VPHM-PID-001/11 | F | 24VPHM-PI-3103 | CHH1 Train-B outlet temperature | Chilled water | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPTM | 0 | 35 | 80 | 50 | 7.62 | 20 | 35 | 77.92 | # 300 | 80S | SIC-2 | QC-2 | SC-1 (S) SL2 | VQC-NA | N/A | N/A | 2 | 1600 | SEP | 35 | 600 | 25 | 1000 | 0.00131 | tapered | 25 | 60 | 65 | 25.4 | 16 | 6.6 | 6.4
66 | 24VP00-MTE-8227 | 24VP00-MTW-8227 | NO | 11-B1-01 | -3.33 | 9.8 | 24VP00-PID-001/03 | G | LLT1-N16 | LLT-1 gas temperature | Air/steam/H2 | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 125 | N/A | 50 | 72 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
67 | 24VP00-MTE-8228 | 24VP00-MTW-8228 | NO | 11-B1-01 | -3.33 | 9.8 | 24VP00-PID-001/03 | G | LLT1-N19 | LLT-1 gas temperature | Air/steam/H2 | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 125 | N/A | 50 | 72 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
68 | 24VP00-MTE-8237 | 24VP00-MTW-8237 | NO | 11-B1-01 | -3.33 | 9.8 | 24VP00-PID-001/04 | G | LLT2-N16 | LLT-2 gas temperature | Air/steam/H2 | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 125 | N/A | 50 | 72 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
69 | 24VP00-MTE-8238 | 24VP00-MTW-8238 | NO | 11-B1-01 | -3.33 | 9.8 | 24VP00-PID-001/04 | G | LLT2-N19 | LLT-2 gas temperature | Air/steam/H2 | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPSM | 6 | 125 | N/A | 50 | 72 | 15 | 125 | N/A | N/A | N/A | SIC-1 | QC-1 | SC1 | N/A | TC1A | N2 | 1 | N/A | IV | Not required | Not required | Not required | Not required | Not required | tapered | 15 | 170 | 200 | 42.2 | 26.5 | 6.5 | 6.4
70 | 24VPRP-MTE-1205 | 24VPRP-MTW-1205 | NO | 11-B1-01 | -3.2 | 9.9 | 24VPRP-PID-001/03 | G | 24VPRP-PI-1016 | Captive relief line DN500 gas temp. | Air/steam/H2 | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPTM | 18 | 230 | 500 | 50 | 12.7 | 0.5 | 250 | 482.6 | # 300 | 80S | SIC-1 | QC-1 | SC-1 (S) SL3 | VQC-2A | TC-2A | N/A | N/A | 250 | N/A | Not required | Not required | Not required | Not required | Not required | tapered | 25 | 65 | 70 | 38 | 29 | 6.6 | 6.4
71 | 24VPRP-MTE-1206 | 24VPRP-MTW-1206 | NO | 11-B1-01 | -3.02 | 10.1 | 24VPRP-PID-001/03 | G | 24VPRP-PI-1017 | Captive relief line DN300 gas temp. | Air/steam/H2 | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPTM | 18 | 230 | 300 | 50 | 12.7 | 0.5 | 250 | 298.4 | # 300 | 80S | SIC-1 | QC-1 | SC-1 (S) SL3 | VQC-2A | TC-2A | N/A | N/A | 150 | N/A | Not required | Not required | Not required | Not required | Not required | tapered | 25 | 65 | 75 | 38 | 29 | 6.6 | 6.4
72 | 24VPHM-MTE-8252 | 24VPHM-MTW-8252 | YES | 11-B1-01 | -2.89 | 10.2 | 24VPHM-PID-001/02 | F | 24VPHM-PI-8052 | LLT vent line temperature | Air/steam/H2 | NON-SIC | QC-2 | 4-Wire RTD PT-100 | 1/2 NPTM | 6 | 100 | 80 | 50 | 7.62 | 20 | 125 | 77.92 | # 300 | 80S | SIC-1 | QC-1 | SC-1 (S) SL2 | VQC-NA | TC-2A | N2 | 1 | 1600 | II | 60 | 100 | 250 | 0.949 | 1.86e-05 | tapered | 25 | 60 | 65 | 25.4 | 16 | 6.6 | 6.4
73 | 24VPRP-MTE-0202 | N/A surface temperature | N/A | 11-L1-CNB |  | N/A | 24VPRP-PID-001/02 | G | 24VPRP-PI-0003 | Captive relief line DN300 pipe temp. | Air/steam/H2 | NON-SIC | QC-2 | Surface 4-Wire RTD To be confirmed | N/A | 18 | 230 | 300 | 50 | 12.7 | 0.5 | 250 | 298.4 | # 300 | 80S | SIC-1 | QC-1 | SC-1 (S) SL3 | VQC-2A | TC-2A | N/A | N/A | 150 | N/A | Not required | Not required | Not required | Not required | Not required | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
74 | 24VPRP-MTE-0204 | N/A surface temperature | N/A | 11-L1-CNB |  | N/A | 24VPRP-PID-001/02 | G | 24VPRP-PI-0003 | Captive relief line DN300 pipe temp. | Air/steam/H2 | NON-SIC | QC-2 | Surface 4-Wire RTD To be confirmed | N/A | 18 | 230 | 300 | 50 | 12.7 | 0.5 | 250 | 298.4 | # 300 | 80S | SIC-1 | QC-1 | SC-1 (S) SL3 | VQC-2A | TC-2A | N/A | N/A | 150 | N/A | Not required | Not required | Not required | Not required | Not required | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
75 | 24VPRP-MTE-0201 | N/A surface temperature | N/A | 11-L1-CNB |  | N/A | 24VPRP-PID-001/02 | G | 24VPRP-PI-0001 | Captive relief line DN500 pipe temp. | Air/steam/H2 | NON-SIC | QC-2 | Surface 4-Wire RTD To be confirmed | N/A | 18 | 230 | 500 | 50 | 12.7 | 0.5 | 250 | 482.6 | # 300 | 80S | SIC-1 | QC-1 | SC-1 (S) SL3 | VQC-2A | TC-2A | N/A | N/A | 250 | N/A | Not required | Not required | Not required | Not required | Not required | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
76 | 24VPRP-MTE-0203 | N/A surface temperature | N/A | 11-L1-CNB |  | N/A | 24VPRP-PID-001/02 | G | 24VPRP-PI-0001 | Captive relief line DN500 pipe temp. | Air/steam/H2 | NON-SIC | QC-2 | Surface 4-Wire RTD To be confirmed | N/A | 18 | 230 | 500 | 50 | 12.7 | 0.5 | 250 | 482.6 | # 300 | 80S | SIC-1 | QC-1 | SC-1 (S) SL3 | VQC-2A | TC-2A | N/A | N/A | 250 | N/A | Not required | Not required | Not required | Not required | Not required | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Note on AF54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pressure equipment connected could be N3. Due to uncertainty, it is kept N2.
Note on AF55: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pressure equipment connected could be N3. Due to uncertainty, it is kept N2.
Note on AF56: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pressure equipment connected could be N3. Due to uncertainty, it is kept N2.
Note on AF57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pressure equipment connected could be N3. Due to uncertainty, it is kept N2.
Note on AF68: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pressure equipment connected could be N3. Due to uncertainty, it is kept N2.