## LIST
|  |  | VVPSS Flow Measurement Datasheet | [6 empty] | Document Nº | BGQXBT
[10 empty] | Revision Nº | 1.4
[10 empty] | Page Nº | 1
1 | SCOPE | [8 empty] | PROCESS DATA | [12 empty] | SENSOR DATA |  |  |  |  | PRIMARY ELEMENT DATA | [6 empty] | PIPE DATA (PRIMARY ELEMENT DESIGN & CLASSIFICATION TO BE ALIGNED ON PIPE)
1 | Sensors | Primary elements | Room number | Estmated absolute elevation (m) | Elevation in DTR (m) | PID | PID version | Connecting line | Measurement description | Process Fluid | Process Dust load | Primary element allowable DP (kPa) | MIN CASE Temperature (℃) | MIN CASE pressure (kPa abs) | MIN CASE flow (Nm3/h) | MIN CASE density (kg/m3) | MIN CASE viscosity (kg/m/s) | MAX CASE Temperature (℃) | MAX CASE pressure (kPa abs) | MAX CASE flow (Nm3/h) | MAX CASE density (kg/m3) | MAX CASE viscosity (kg/m/s) | Sensor safety class | Sensor quality class | Recommended sensor type | Sensor connection type | Sensor range | Available straigth pipe length (mm) | Flow conditioning recommended | Preliminary sizing of primary element restriction diameter (mm) | Recommended type of primary element | Number of taping points for sensor lines | Connection type to sensor lines | Connection type to process pipe | DN | Insul. Thick. (mm) | PS (barg) | Td (deg) | Pipe ID (mm) | Piping class | Piping schedule | Piping thickness (mm) | Pipe Safety Class | Pipe quality class | Pipe seismic class | Pipe Vacuum class | Pipe tritium class | Pipe ESPN class | F. Group | PSxDN | Pipe PED Category
2 | 24VP00-MFT-3201 | 24VP00-DIM-3201 | 11-B2-01 | -13.09 | 0 | 24VP00-PID-001/02 | G | 24VP00-PI-3301 | SLT CHW cooling flow | Chilled Water | CLEAN | 50 | 5 | 1000 | 2 | 1000 | 0.00179 | 13 | 600 | 4 | 1000 | 0.001306 | NON-SIC | QC-2 | MPD | 2 x 1/4 NPTM | 0-1bar | to be confirmed | Vendor to confirm | 10.8 | orifice with meter run | 2 | Vendor to confirm | flange | 25 | 25 | 15 | 35 | 27.86 | # 300 | 10 | 2.77 | NON-SIC | QC-3 | SC-1 (S) SL2 | VQC-NA | N/A | N/A | 2 | 375 | SEP
3 | 24VP00-MFT-1213 | 24VP00-DIM-1213 | 11-B2-01 | -13.09 | 0 | 24VP00-PID-001/02 | G | 24VP00-PI-1311 | SLT cooling coil flow | Demineralized water | CLEAN | 50 | 6 | 500 | 7 | 1000 | 0.001791 | 35 | 100 | 22 | 1000 | 0.000797 | NON-SIC | QC-2 | MPD | 2 x 1/4 NPTM | 0-1bar | 737 to be confirmed | Vendor to confirm | 23.7 | orifice with meter run | 2 | Vendor to confirm | flange | 50 | 25 | 15 | 125 | 49.22 | # 300 | 80S | 5.54 | SIC-2 | QC-1 | SC-1 (S) SL2 | VQC-NA | TC-2A | N2 | 1 | 750 | SEP
4 | 24VPHM-MFT-8274 | 24VPHM-DIM-8274 | 11-B2-01 | -9.896 | 3.2 | 24VPHM-PID-001/05 | F | 24VPHM-PI-8080 | SLT reflux flow | Tritiated water | DIRTY | 50 | 6 | 800 | 2 | 1000 | 0.00179 | 60 | 84 | 6 | 1000 | 0.000466 | NON-SIC | QC-2 | MPD | 2 x 1/2 VCR | 0-1bar | 477 to be confirmed | Vendor to confirm | 10.2 | orifice with meter run | 2 | buttweld tubing OD 12.7 mm / tck 1.245 mm | butt welded | 25 | N/A | 20 | 125 | 24.3 | # 300 | 80S | 4.55 | SIC-1 | QC-1 | SC-1 (S) SL2 | VQC-NA | TC-2A | N2 | 1 | 500 | SEP
5 | 24VPHM-MFT-3200 | 24VPHM-DIM-3200 | 11-B1-01 | -7.87 | 5.2 | 24VPHM-PID-001/11 | F | 24VPHM-PI-3001 | EXC train A CHW flow | Chilled Water | CLEAN | 50 | 5 | 1000 | 8 | 1000 | 0.001791 | 35 | 600 | 25 | 1000 | 0.001306 | NON-SIC | QC-2 | MPD | 2 x 1/4 NPTM | 0-1bar | 2434 to be confirmed | Vendor to confirm | 30.5 | orifice with meter run | 2 | Vendor to confirm | flange | 65 | 50 | 20 | 35 | 66.9 | # 300 | 10 | 3.05 | SIC-2 | QC-2 | SC-1 (S) SL2 | VQC-NA | N/A | N/A | 2 | 1300 | SEP
6 | 24VPHM-MFT-3040 | 24VPHM-DIM-3040 | 11-B1-01 | -7.87 | 5.2 | 24VPHM-PID-001/11 | F | 24VPHM-PI-3003 | PST coil train A CHW flow | Chilled Water | CLEAN | 50 | 5 | 1000 | 8 | 1000 | 0.001791 | 35 | 600 | 25 | 1000 | 0.001306 | SIC-2 | QC-1 | MPD | 2 x 1/4 NPTM | 0-1bar | 1606 to be confirmed | Vendor to confirm | 30.5 | orifice with meter run | 2 | Vendor to confirm | flange | 65 | 50 | 20 | 35 | 66.9 | # 300 | 10 | 3.05 | SIC-2 | QC-2 | SC-1 (S) SL2 | VQC-NA | N/A | N/A | 2 | 1300 | SEP
7 | 24VPHM-MFT-8271 | 24VPHM-DIM-8271 | 11-B1-01 | -7.76 | 5.3 | 24VPHM-PID-001/03 | F | 24VPHM-PI-8061 | WRC inlet gas flow | AIR / STEAM/ H2 | DIRTY | 1 | 6 | 115 | 350 | 1.369 | 1.686e-05 | 100 | 70 | 600 | 0.698 | 1.909e-05 | NON-SIC | QC-2 | MPD | 2 x 1/2 VCR | 0-100mbar | 500 to be confirmed | YES | 70.4 | Long-radius nozzle or wedge meter | 2 | buttweld tubing OD 12.7 mm / tck 1.245 mm | butt welded | 150 | 25 | 20 | 125 | 146.36 | # 300 | 80S | 10.97 | SIC-1 | QC-1 | SC-1 (S) SL2 | VQC-NA | TC-2A | N2 | 1 | 3000 | II
8 | 24VP00-MFT-4203 | 24VP00-DIM-4203 | 11-B1-01 | -6.313 | 6.8 | 24VP00-PID-001/07 | G | 24VP00-PI-4301 | VP00 DMW flow | Demineralized water | CLEAN | 50 | 6 | 1000 | 4 | 1000 | 0.000797 | 35 | 600 | 11 | 1000 | 0.001791 | NON-SIC | QC-2 | MPD | 2 x 1/4 NPTM | 0-1bar | 649 to be confirmed | Vendor to confirm | 26.4 | orifice with meter run | 2 | Vendor to confirm | flange | 80 | N/A | 15 | 65 | 82.8 | # 300 | 10 | 3.05 | NON-SIC | QC-3 | SC-1 (S) SL2 | VQC-NA | N/A | N/A | 2 | 1200 | SEP
9 | 24VPHM-MFT-1059 24VPHM-MFT-1159 | 24VPHM-DIM-1259 | 11-B1-01 | -5.89 | 7.2 | 24VPHM-PID-001/02 | F | 24VPHM-PI-1059 | PST Dilution air flow | Air | CLEAN | 2 | 18 | 100 | 117 | 1.199 | 1.73e-05 | 35 | 90 | 385 | 1.019 | 1.82e-05 | SIC-2 | QC-1 | MPD | 2 x 1/4 NPTM | 0-100mbar | 1051 | Vendor to confirm | 39.9 | orifice with meter run | 4 | Vendor to confirm | flange | 80 | 50 | 20 | 125 | 77.92 | # 300 | 80S | 7.62 | SIC-1 | QC-1 | SC-1 (S) SL2 | VQC-NA | TC-2A | N/A | N/A | N/A | N/A
10 | 24VPHM-MFT-5022 | 24VPHM-DIM-5022 | 11-B1-01 | -5.23 | 7.9 | 24VPHM-PID-001/12 | F | 24VPHM-PI-5101 | VPHM nitrogen flow | Nitrogen Gas | CLEAN | 50 | 18 | 800 | 20 | 9.259 | 1.66e-05 | 35 | 600 | 50 | 6.561 | 1.76e-05 | SIC-2 | QC-1 | MPD | 2 x 1/4 NPTM | 0-1bar | 1176 | Vendor to confirm | 8.8 | orifice with meter run | 2 | Vendor to confirm | flange | 25 | 50 | 20 | 65 | 27.86 | # 300 | 10 | 2.77 | SIC-2 | QC-2 | SC-1 (S) SL2 | VQC-NA | N/A | N2 | 2 | 500 | SEP
11 | 24VPHM-MFT-8273 | 24VPHM-DIM-8273 | 11-B2-01 | -4.45 | 8.6 | 24VPHM-PID-001/05 | F | 24VPHM-PI-8074 | WRC reflux flow | Tritiated water | DIRTY | 50 | 6 | 800 | 2 | 1000 | 0.00179 | 60 | 84 | 6 | 1000 | 0.000466 | NON-SIC | QC-2 | MPD | 2 x 1/2 VCR | 0-1bar | 1549 to be confirmed | Vendor to confirm | 10.2 | orifice with meter run | 2 | buttweld tubing OD 12.7 mm / tck 1.245 mm | butt welded | 25 | 50 | 20 | 125 | 24.3 | # 300 | 80S | 4.55 | SIC-1 | QC-1 | SC-1 (S) SL2 | VQC-NA | TC-2A | N2 | 1 | 500 | SEP
13 | 24VPHM-MFT-1250 | 24VPHM-DI-1050 | 11-B1-01 | -4.44 | 8.7 | 24VPHM-PID-001/02 | F | 24VPHM-PI-1050 | PST HMS-01 flow | AIR / STEAM/ H2 | DIRTY | N/A | 18 | 100 | 100 | 1.179 | 1.716e-05 | 230 | 87 | 350 | 0.489 | 2.078e-05 | NON-SIC | QC-2 | MPD | 2 x 1/2 VCR | 0-100mbar | 3724 | Vendor to confirm | 40 | HMS-01 Restrictor - Geometry fully imposed - refer specification | 2 | buttweld tubing OD 12.7 mm / tck 1.245 mm | butt welded | 80 | 50 | 15 | 250 | 77.92 | # 300 | 80S | 7.62 | SIC-1 | QC-1 | SC-1 (S) SL3 | VQC-3A | TC-2A | N2 | 1 | 1200 | II
14 | 24VP00-MFT-8134 | 24VP00-DIM-8134 | 11-B1-01 | -4.21 | 8.9 | 24VP00-PID-001/04 | G | 24VP00-PI-8134 | LLT2 ejctor motive flow | Nitrogen Gas | CLEAN | 50 | 18 | 800 | 10 | 9.259 | 1.66e-05 | 35 | 600 | 40 | 6.561 | 1.76e-05 | SIC-2 | QC-1 | MPD | 2 x 1/4 NPTM | 0-1bar | 842 | Vendor to confirm | 8.6 | orifice with meter run | 2 | Vendor to confirm | flange | 25 | 50 | 15 | 65 | 27.86 | # 300 | 10 | 2.77 | SIC-2 | QC-2 | SC-1 (S) SL2 | VQC-NA | N/A | N2 | 2 | 375 | SEP
15 | 24VPHM-MFT-3201 | 24VPHM-DIM-3201 | 11-B1-01 | -4.22 | 8.9 | 24VPHM-PID-001/11 | F | 24VPHM-PI-3101 | EXC train B CHW flow | Chilled Water | CLEAN | 50 | 5 | 1000 | 8 | 1000 | 0.001791 | 35 | 600 | 25 | 1000 | 0.001306 | NON-SIC | QC-2 | MPD | 2 x 1/4 NPTM | 0-1bar | 1574 to be confirmed | Vendor to confirm | 30.5 | orifice with meter run | 2 | Vendor to confirm | flange | 65 | 50 | 20 | 35 | 66.9 | # 300 | 10 | 3.05 | SIC-2 | QC-2 | SC-1 (S) SL2 | VQC-NA | N/A | N/A | 2 | 1300 | SEP
16 | 24VPHM-MFT-3140 | 24VPHM-DIM-3140 | 11-B1-01 | -3.78 | 9.3 | 24VPHM-PID-001/11 | F | 24VPHM-PI-3103 | PST coil train B CHW flow | Chilled Water | CLEAN | 50 | 5 | 1000 | 8 | 1000 | 0.001791 | 35 | 600 | 25 | 1000 | 0.001306 | SIC-2 | QC-1 | MPD | 2 x 1/4 NPTM | 0-1bar | 1896 to be confirmed | Vendor to confirm | 30.5 | orifice with meter run | 2 | Vendor to confirm | flange | 65 | 50 | 20 | 35 | 66.9 | # 300 | 10 | 3.05 | SIC-2 | QC-2 | SC-1 (S) SL2 | VQC-NA | N/A | N/A | 2 | 1300 | SEP
17 | 24VP00-MFT-8144 | 24VP00-DIM-8144 | 11-B1-01 | -3.738 | 9.4 | 24VP00-PID-001/05 | G | 24VP00-PI-8144 | LLT3 ejctor motive flow | Nitrogen Gas | CLEAN | 50 | 18 | 800 | 10 | 9.259 | 1.66e-05 | 35 | 600 | 40 | 6.561 | 1.76e-05 | SIC-2 | QC-1 | MPD | 2 x 1/4 NPTM | 0-1bar | 1404 | Vendor to confirm | 8.6 | orifice with meter run | 2 | Vendor to confirm | flange | 25 | 50 | 15 | 65 | 27.86 | # 300 | 10 | 2.77 | SIC-2 | QC-2 | SC-1 (S) SL2 | VQC-NA | N/A | N2 | 2 | 375 | SEP
18 | 24VPHM-MFT-4221 | 24VPHM-DIM-4221 | 11-B1-01 | -3.58 | 9.5 | 24VPHM-PID-001/15 | F | 24VPHM-PI-4301 | VPHM DMW flow | Demineralized water | CLEAN | 50 | 6 | 1000 | 4 | 1000 | 0.000797 | 35 | 600 | 11 | 1000 | 0.001791 | NON-SIC | QC-2 | MPD | 2 x 1/4 NPTM | 0-1bar | 1687 to be confirmed | Vendor to confirm | 26.4 | orifice with meter run | 2 | Vendor to confirm | flange | 80 | N/A | 15 | 65 | 82.8 | # 300 | 10 | 3.05 | NON-SIC | QC-3 | SC-1 (S) SL2 | VQC-NA | N/A | N/A | 2 | 1200 | SEP
19 | 24VP00-MFT-8014 | 24VP00-DIM-8014 | 11-B1-01 | -3.368 | 9.7 | 24VP00-PID-001/02 | G | 24VP00-PI-8014 | SLT ejector motive flow | Nitrogen Gas | CLEAN | 50 | 18 | 800 | 10 | 9.259 | 1.66e-05 | 35 | 600 | 40 | 6.561 | 1.76e-05 | SIC-2 | QC-1 | MPD | 2 x 1/4 NPTM | 0-1bar | 1102 | Vendor to confirm | 8.6 | orifice with meter run | 2 | Vendor to confirm | flange | 25 | 50 | 15 | 65 | 27.86 | # 300 | 10 | 2.77 | SIC-2 | QC-2 | SC-1 (S) SL2 | VQC-NA | N/A | N2 | 2 | 375 | SEP
20 | 24VP00-MFT-8024 | 24VP00-DIM-8024 | 11-B1-01 | -3.142 | 9.9 | 24VP00-PID-001/03 | G | 24VP00-PI-8024 | LLT1 ejctor motive flow | Nitrogen Gas | CLEAN | 50 | 18 | 800 | 10 | 9.259 | 1.66e-05 | 35 | 600 | 40 | 6.561 | 1.76e-05 | SIC-2 | QC-1 | MPD | 2 x 1/4 NPTM | 0-1bar | 1869 | Vendor to confirm | 8.6 | orifice with meter run | 2 | Vendor to confirm | flange | 25 | 50 | 15 | 65 | 27.86 | # 300 | 10 | 2.77 | SIC-2 | QC-2 | SC-1 (S) SL2 | VQC-NA | N/A | N2 | 2 | 375 | SEP
21 | 24VPHM-MFT-8252 | 24VPHM-DIM-8252 | 11-B1-01 | -2.89 | 10.2 | 24VPHM-PID-001/02 | F | 24VPHM-PI-8052 | PST HMS-02 flow | AIR / STEAM/ H2 | DIRTY | 2 | 6 | 180 | 60 | 2.038 | 1.641e-05 | 60 | 100 | 250 | 0.949 | 1.858e-05 | NON-SIC | QC-2 | MPD | 2 x 1/2 VCR | 0-100mbar | 2729 | Vendor to confirm | 33 | Long-radius nozzle or wedge meter | 2 | buttweld tubing OD 12.7 mm / tck 1.245 mm | butt welded | 80 | 50 | 20 | 125 | 77.92 | # 300 | 80S | 7.62 | SIC-1 | QC-1 | SC-1 (S) SL2 | VQC-NA | TC-2A | N2 | 1 | 1600 | II
22 | 24VPHM-MFT-1091 24VPHM-MFT-1191 | 24VPHM-DIM-1291 | 11-L3-02E |  | N/A | 24VPHM-PID-001/08 | F | 24VPHM-PI-1093 | HMS exhaust flow | AIR / STEAM/ H2 | DIRTY | 1 | 6 | 100 | 350 | 1.198 | 1.721e-05 | 35 | 70 | 600 | 0.784 | 1.811e-05 | SIC-2 | QC-1 | MPD | 2 x 1/2 VCR | 0-100mbar | 3746 | Vendor to confirm | 66.1 | Long-radius nozzle or wedge meter | 4 | buttweld tubing OD 12.7 mm / tck 1.245 mm | butt welded | 150 | 50 | 0.5 | 80 | 146.36 | # 300 | 80S | 10.97 | SIC-1 | QC-1 | SC-1 (S) SL2 | VQC-NA | TC-2A | N/A | N/A | N/A | N/A
Note on E7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Assumed in lower temperature fire zone
Note on E9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Elevation reflux nozzle N15 on SLT
Note on M14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Could be a bit larger but this is the initial request for technical investigation
Note on E16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Estimated elevation top of recombiner
Note on C17: Giametta Roxane: HMS-01 restrictor
Note on M17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Refer to HMS-01 restrictor experimental pressure drop curve. We fully impose the primary element geometry and the pressure drop will be the result. The vendor will manufacture the restrictor as per the specification with pressure tapings and calibrate the flow measurement.
Note on M25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Investigation of a technical solution minimizing the pressure drop for the option where we will delete the downstream HMS-02 restrictor.